## Data
Plant | 1C Mill
Date | 2011-09-26
Run number | 63 T/hr
Operator | DK | [6 empty] | DELTA T | 4.5 | wa KG/M³ | 1.2335
Results
Average Duct Temperature | 265.5535 | °C |  | Indicated Airflow
Average duct gas velocity | 11.3203 | m/s |  | CCR DCS | 62.8 |  |  | WBT R | 509 | Pv | 0.87439
Duct Flow Rate | 25.1353 | cu m/s
Mass Flow | 17.1853 | kg/s |  | Start Time | 11:17 |  |  | LOG Psat | -0.76706 | Psat kPa | 1.1789
| 61.8671 | tonnes/hr |  | End Time | 11:40
Average Piccolo Tx Current | 10.3334 | mA
Piccolo Tx Range Setting | 6.7 | mbar | [5 empty] | Average Static | 4024.6357 | Pa
Average Piccolo Tx Pressure | 2.6521 | mbar | [5 empty] | Average Duct temp | 265.5535 | C
Port 1 |  |  |  |  | Barometric pressure | kPa | 101.6
Velocity pressure | Pa | 66.7506 |  |  | Dry bulb temperature | C | 14 | 0.17909
Static pressure | Pa | 3938.4249 |  |  | Wet bulb temperature | C | 9.5
Duct Temperature | °C | 275.1252 |  |  | Air density | kg/m3 | 1.2335
Square root velocity pressure | sqrt(kPa) | 0.25836
Average transverse gas velocity | m/s | 12.8213 |  |  | Duct
[5 empty] | Duct Height | m | 0.955
Port 2 |  |  |  |  | Duct Width | m | 2.325
Velocity pressure | Pa | 62.8707 |  |  | Stack Area | m2 | 2.2204
Static pressure | Pa | 4015.6189 |  |  | Duct gas density | kg/m3 | 0.68371
Duct Temperature | °C | 271.6097 |  |  | Pitot tube calibration factor | - | 0.997
Square root velocity pressure | sqrt(kPa) | 0.25074
Average transverse gas velocity | m/s | 14.5911 | Comment
Follow up test after the AF Tx was re-ranged to 6.7 mBar.
Port 3
Velocity pressure | Pa | 56.6005
Static pressure | Pa | 4098.6721
Duct Temperature | °C | 267.1928
Square root velocity pressure | sqrt(kPa) | 0.23791
Average transverse gas velocity | m/s | 12.4134
Port 4
Velocity pressure | Pa | 42.5473
Static pressure | Pa | 4108.7321
Duct Temperature | °C | 263.5804
Square root velocity pressure | sqrt(kPa) | 0.20627
Average transverse gas velocity | m/s | 12.5071
Port 5
Velocity pressure | Pa | 26.3811
Static pressure | Pa | 4044.8383
Duct Temperature | °C | 261.1494
Square root velocity pressure | sqrt(kPa) | 0.16242
Average transverse gas velocity | m/s | 6.7964
Port 6
Velocity pressure | Pa | 33.6813
Static pressure | Pa | 4056.0508
Duct Temperature | °C | 260.9296
Square root velocity pressure | sqrt(kPa) | 0.18352
Average transverse gas velocity | m/s | 9.1999
Port 7
Velocity pressure | Pa | 46.3857
Static pressure | Pa | 3975.7898
Duct Temperature | °C | 261.5374
Square root velocity pressure | sqrt(kPa) | 0.21537
Average transverse gas velocity | m/s | 11.849
Port 8
Velocity pressure | Pa | 55.9654
Static pressure | Pa | 3958.9584
Duct Temperature | °C | 263.3035
Square root velocity pressure | sqrt(kPa) | 0.23657
Average transverse gas velocity | m/s | 10.3842

## P1
| Port | 1
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current
| Pa | Pa | Deg C | mA
Averages | 3938.4249 | 66.7506 | 275.1252 | 10.2866 | [11 empty] | 12.8213 |  | 12.8153
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current |  |  |  |  | a | b | n | h | xi | f(xi) | Aj
| Pa. | Pa | Deg C | mA |  | 13.9772 |  |  | 0 | 1 | 100 | 0.01 | 0 | 7.7079
[6 empty] | vel | dens | [5 empty] | 0.01 | 7.7079 | 0.077079 |  | 0.15416 |  | 26.5
11:17 | 3964 | 20 | 273.7 | 10.3 | 1 | 7.7079 | 0.67353 | 7.9981 |  |  |  |  | 0.02 | 7.7079 | 0.077079 |  |  |  | 26.5
11:17 | 3965 | 20 | 273.7 | 10.3 | 2 | 7.7079 | 0.67353 | 8.2066 |  |  |  |  | 0.03 | 7.8982 | 0.078031 |  | 0.15733 |  | 27.5
11:17 | 3974 | 20 | 273.7 | 10.3 | 3 | 7.7079 | 0.67353 | 8.4116 |  |  |  |  | 0.04 | 7.8982 | 0.078982 |  |  |  | 28.5
11:17 | 3974 | 21 | 273.7 | 10.3 | 4 | 7.8982 | 0.67353 | 8.6131 |  |  |  |  | 0.05 | 8.0834 | 0.079908 |  | 0.16105 |  | 29.5
11:17 | 3991 | 21 | 273.7 | 10.3 | 5 | 7.8982 | 0.67353 | 8.8111 |  |  |  |  | 0.06 | 8.0834 | 0.080834 |  |  |  | 31.5
11:17 | 3991 | 22 | 273.6 | 10.3 | 6 | 8.0834 | 0.67365 | 9.0057 |  |  |  |  | 0.07 | 8.2658 | 0.081746 |  | 0.1653 |  | 32
11:17 | 3984 | 22 | 273.6 | 10.3 | 7 | 8.0834 | 0.67365 | 9.1968 |  |  |  |  | 0.08 | 8.4436 | 0.083547 |  |  |  | 36
11:17 | 3979 | 23 | 273.7 | 10.3 | 8 | 8.2658 | 0.67353 | 9.3846 |  |  |  |  | 0.09 | 8.7892 | 0.086164 |  | 0.17463 |  | 36.5
11:17 | 3980 | 24 | 273.7 | 10.3 | 9 | 8.4436 | 0.67353 | 9.5689 |  |  |  |  | 0.1 | 8.7892 | 0.087892 |  |  |  | 41.5
11:17 | 3981 | 26 | 273.8 | 10.3 | 10 | 8.7892 | 0.67341 | 9.75 |  |  |  |  | 0.11 | 9.4411 | 0.091151 |  | 0.18868 |  | 41.5
11:17 | 3981 | 26 | 273.8 | 10.3 | 11 | 8.7892 | 0.67341 | 9.9277 |  |  |  |  | 0.12 | 10.0517 | 0.097464 |  |  |  | 45
11:17 | 3983 | 30 | 273.8 | 10.3 | 12 | 9.4411 | 0.67341 | 10.1021 |  |  |  |  | 0.13 | 9.9028 | 0.099772 |  | 0.19856 |  | 48
11:17 | 3983 | 34 | 273.9 | 10.3 | 13 | 10.0517 | 0.67328 | 10.2733 |  |  |  |  | 0.14 | 9.9055 | 0.099041 |  |  |  | 47
11:17 | 3986 | 33 | 273.9 | 10.3 | 14 | 9.9028 | 0.67328 | 10.4412 |  |  |  |  | 0.15 | 9.9055 | 0.099055 |  | 0.20189 |  | 47
11:17 | 3986 | 33 | 274.2 | 10.3 | 15 | 9.9055 | 0.67291 | 10.6059 |  |  |  |  | 0.16 | 11.0401 | 0.10473 |  |  |  | 47
11:17 | 3987 | 33 | 274.2 | 10.3 | 16 | 9.9055 | 0.67291 | 10.7675 |  |  |  |  | 0.17 | 11.0391 | 0.1104 |  | 0.22502 |  | 51
11:17 | 3988 | 41 | 274.1 | 10.3 | 17 | 11.0401 | 0.67304 | 10.9259 |  |  |  |  | 0.18 | 12.3108 | 0.11675 |  |  |  | 51
11:17 | 3989 | 41 | 274 | 10.3 | 18 | 11.0391 | 0.67316 | 11.0811 |  |  |  |  | 0.19 | 12.3096 | 0.1231 |  | 0.24739 |  | 55
11:17 | 3990 | 51 | 273.9 | 10.3 | 19 | 12.3108 | 0.67328 | 11.2333 |  |  |  |  | 0.2 | 12.6665 | 0.12488 |  |  |  | 55
11:17 | 3989 | 51 | 273.8 | 10.4 | 20 | 12.3096 | 0.67341 | 11.3823 |  |  |  |  | 0.21 | 13.0136 | 0.1284 |  | 0.25796 |  | 58
11:17 | 3978 | 54 | 273.8 | 10.4 | 21 | 12.6665 | 0.67341 | 11.5284 |  |  |  |  | 0.22 | 12.6665 | 0.1284 |  |  |  | 61
11:17 | 3977 | 57 | 273.8 | 10.3 | 22 | 13.0136 | 0.67341 | 11.6714 |  |  |  |  | 0.23 | 12.3119 | 0.12489 |  | 0.24742 |  | 60
11:17 | 3961 | 54 | 273.8 | 10.3 | 23 | 12.6665 | 0.67341 | 11.8114 |  |  |  |  | 0.24 | 12.3119 | 0.12312 |  |  |  | 59
11:17 | 3961 | 51 | 274 | 10.3 | 24 | 12.3119 | 0.67316 | 11.9484 |  |  |  |  | 0.25 | 12.7856 | 0.12549 |  | 0.25413 |  | 59.5
11:17 | 3953 | 51 | 274 | 10.3 | 25 | 12.3119 | 0.67316 | 12.0825 |  |  |  |  | 0.26 | 12.7856 | 0.12786 |  |  |  | 64
11:17 | 3947 | 55 | 274 | 10.3 | 26 | 12.7856 | 0.67316 | 12.2137 |  |  |  |  | 0.27 | 12.9013 | 0.12843 |  | 0.25764 |  | 64
11:17 | 3945 | 55 | 274 | 10.3 | 27 | 12.7856 | 0.67316 | 12.342 |  |  |  |  | 0.28 | 12.9013 | 0.12901 |  |  |  | 68
11:17 | 3944 | 56 | 274 | 10.3 | 28 | 12.9013 | 0.67316 | 12.4674 |  |  |  |  | 0.29 | 13.016 | 0.12959 |  | 0.26033 |  | 68
11:17 | 3945 | 56 | 274 | 10.3 | 29 | 12.9013 | 0.67316 | 12.59 |  |  |  |  | 0.3 | 13.1333 | 0.13075 |  |  |  | 68
11:17 | 3954 | 57 | 274 | 10.3 | 30 | 13.016 | 0.67316 | 12.7097 |  |  |  |  | 0.31 | 13.7959 | 0.13465 |  | 0.27582 |  | 68
11:17 | 3954 | 58 | 274.3 | 10.3 | 31 | 13.1333 | 0.67279 | 12.8267 |  |  |  |  | 0.32 | 14.4307 | 0.14113 |  |  |  | 71
11:17 | 3951 | 64 | 274.3 | 10.3 | 32 | 13.7959 | 0.67279 | 12.941 |  |  |  |  | 0.33 | 14.4307 | 0.14431 |  | 0.28896 |  | 74
11:17 | 3951 | 70 | 274.5 | 10.3 | 33 | 14.4307 | 0.67255 | 13.0525 |  |  |  |  | 0.34 | 14.5347 | 0.14483 |  |  |  | 74.5
11:17 | 3945 | 70 | 274.5 | 10.3 | 34 | 14.4307 | 0.67255 | 13.1613 |  |  |  |  | 0.35 | 14.5347 | 0.14535 |  | 0.29036 |  | 78
11:17 | 3941 | 71 | 274.6 | 10.4 | 35 | 14.5347 | 0.67242 | 13.2674 |  |  |  |  | 0.36 | 14.4333 | 0.14484 |  |  |  | 78
11:17 | 3937 | 71 | 274.6 | 10.4 | 36 | 14.5347 | 0.67242 | 13.3709 |  |  |  |  | 0.37 | 14.4346 | 0.14434 |  | 0.28834 |  | 76.5
11:17 | 3933 | 70 | 274.7 | 10.4 | 37 | 14.4333 | 0.6723 | 13.4718 |  |  |  |  | 0.38 | 14.3312 | 0.14383 |  |  |  | 76
11:17 | 3933 | 70 | 274.8 | 10.4 | 38 | 14.4346 | 0.67218 | 13.57 |  |  |  |  | 0.39 | 14.2243 | 0.14278 |  | 0.28519 |  | 75.5
11:17 | 3933 | 69 | 274.8 | 10.4 | 39 | 14.3312 | 0.67218 | 13.6657 |  |  |  |  | 0.4 | 14.3286 | 0.14276 |  |  |  | 74.5
11:17 | 3933 | 68 | 274.6 | 10.3 | 40 | 14.2243 | 0.67242 | 13.7588 |  |  |  |  | 0.41 | 14.5334 | 0.14431 |  | 0.28999 |  | 76
11:17 | 3934 | 69 | 274.6 | 10.3 | 41 | 14.3286 | 0.67242 | 13.8495 |  |  |  |  | 0.42 | 14.5334 | 0.14533 |  |  |  | 78
11:17 | 3934 | 71 | 274.5 | 10.3 | 42 | 14.5334 | 0.67255 | 13.9376 |  |  |  |  | 0.43 | 14.6314 | 0.14582 |  | 0.29229 |  | 78
11:17 | 3929 | 71 | 274.5 | 10.3 | 43 | 14.5334 | 0.67255 | 14.0233 |  |  |  |  | 0.44 | 14.6287 | 0.1463 |  |  |  | 77.5
11:17 | 3926 | 72 | 274.2 | 10.3 | 44 | 14.6314 | 0.67291 | 14.1065 |  |  |  |  | 0.45 | 15.226 | 0.14927 |  | 0.30253 |  | 77.5
11:17 | 3920 | 72 | 274 | 10.3 | 45 | 14.6287 | 0.67316 | 14.1874 |  |  |  |  | 0.46 | 15.2247 | 0.15225 |  |  |  | 79
11:17 | 3913 | 78 | 274 | 10.3 | 46 | 15.226 | 0.67316 | 14.2658 |  |  |  |  | 0.47 | 15.3219 | 0.15273 |  | 0.30644 |  | 79
11:17 | 3912 | 78 | 273.9 | 10.3 | 47 | 15.2247 | 0.67328 | 14.3419 |  |  |  |  | 0.48 | 15.4186 | 0.1537 |  |  |  | 79
11:17 | 3903 | 79 | 273.9 | 10.3 | 48 | 15.3219 | 0.67328 | 14.4157 |  |  |  |  | 0.49 | 15.4186 | 0.15419 |  | 0.30807 |  | 79.5
11:17 | 3903 | 80 | 273.9 | 10.3 | 49 | 15.4186 | 0.67328 | 14.4871 |  |  |  |  | 0.5 | 15.3275 | 0.15373 |  |  |  | 78.5
11:17 | 3891 | 80 | 273.9 | 10.3 | 50 | 15.4186 | 0.67328 | 14.5563 |  |  |  |  | 0.51 | 15.3275 | 0.15328 |  | 0.30457 |  | 77
11:17 | 3890 | 79 | 274.3 | 10.3 | 51 | 15.3275 | 0.67279 | 14.6232 |  |  |  |  | 0.52 | 14.734 | 0.15031 |  |  |  | 77
11:17 | 3886 | 79 | 274.3 | 10.3 | 52 | 15.3275 | 0.67279 | 14.6879 |  |  |  |  | 0.53 | 14.7326 | 0.14733 |  | 0.29566 |  | 76.5
11:17 | 3882 | 73 | 274.3 | 10.2 | 53 | 14.734 | 0.67279 | 14.7505 |  |  |  |  | 0.54 | 15.0337 | 0.14883 |  |  |  | 76.5
11:17 | 3892 | 73 | 274.2 | 10.2 | 54 | 14.7326 | 0.67291 | 14.8108 |  |  |  |  | 0.55 | 15.1323 | 0.15083 |  | 0.30232 |  | 77.5
11:17 | 3904 | 76 | 274.3 | 10.2 | 55 | 15.0337 | 0.67279 | 14.869 |  |  |  |  | 0.56 | 15.1323 | 0.15132 |  |  |  | 77.5
11:17 | 3905 | 77 | 274.3 | 10.2 | 56 | 15.1323 | 0.67279 | 14.9251 |  |  |  |  | 0.57 | 15.1337 | 0.15133 |  | 0.30267 |  | 77
11:17 | 3923 | 77 | 274.3 | 10.3 | 57 | 15.1323 | 0.67279 | 14.9791 |  |  |  |  | 0.58 | 15.1337 | 0.15134 |  |  |  | 76
11:17 | 3923 | 77 | 274.4 | 10.2 | 58 | 15.1337 | 0.67267 | 15.031 |  |  |  |  | 0.59 | 15.1337 | 0.15134 |  | 0.30267 |  | 75.5
11:17 | 3936 | 77 | 274.4 | 10.2 | 59 | 15.1337 | 0.67267 | 15.0809 |  |  |  |  | 0.6 | 15.1337 | 0.15134 |  |  |  | 74.5
11:17 | 3937 | 77 | 274.4 | 10.2 | 60 | 15.1337 | 0.67267 | 15.1287 |  |  |  |  | 0.61 | 15.4256 | 0.1528 |  | 0.30753 |  | 74.5
11:17 | 3943 | 77 | 274.4 | 10.2 | 61 | 15.1337 | 0.67267 | 15.1746 |  |  |  |  | 0.62 | 15.4242 | 0.15425 |  |  |  | 74.5
11:17 | 3948 | 80 | 274.4 | 10.2 | 62 | 15.4256 | 0.67267 | 15.2186 |  |  |  |  | 0.63 | 15.233 | 0.15329 |  | 0.30531 |  | 74.5
11:17 | 3945 | 80 | 274.3 | 10.3 | 63 | 15.4242 | 0.67279 | 15.2606 |  |  |  |  | 0.64 | 15.2358 | 0.15234 |  |  |  | 74
11:17 | 3942 | 78 | 274.5 | 10.3 | 64 | 15.233 | 0.67255 | 15.3007 |  |  |  |  | 0.65 | 14.9399 | 0.15088 |  | 0.29878 |  | 74
11:17 | 3942 | 78 | 274.7 | 10.2 | 65 | 15.2358 | 0.6723 | 15.3389 |  |  |  |  | 0.66 | 14.6381 | 0.14789 |  |  |  | 72.5
11:17 | 3953 | 75 | 274.7 | 10.2 | 66 | 14.9399 | 0.6723 | 15.3753 |  |  |  |  | 0.67 | 14.6381 | 0.14638 |  | 0.29311 |  | 71
11:17 | 3953 | 72 | 274.7 | 10.2 | 67 | 14.6381 | 0.6723 | 15.4098 |  |  |  |  | 0.68 | 14.7421 | 0.1469 |  |  |  | 71
11:17 | 3961 | 72 | 274.7 | 10.2 | 68 | 14.6381 | 0.6723 | 15.4426 |  |  |  |  | 0.69 | 14.7421 | 0.14742 |  | 0.29584 |  | 71.5
11:17 | 3962 | 73 | 274.9 | 10.2 | 69 | 14.7421 | 0.67205 | 15.4736 |  |  |  |  | 0.7 | 15.0406 | 0.14891 |  |  |  | 71.5
11:17 | 3958 | 73 | 274.9 | 10.2 | 70 | 14.7421 | 0.67205 | 15.5028 |  |  |  |  | 0.71 | 15.0392 | 0.1504 |  | 0.29978 |  | 72.5
11:17 | 3954 | 76 | 274.8 | 10.2 | 71 | 15.0406 | 0.67218 | 15.5304 |  |  |  |  | 0.72 | 14.738 | 0.14889 |  |  |  | 72.5
11:17 | 3948 | 76 | 274.7 | 10.3 | 72 | 15.0392 | 0.6723 | 15.5562 |  |  |  |  | 0.73 | 14.6367 | 0.14687 |  | 0.29408 |  | 71
11:17 | 3941 | 73 | 274.6 | 10.3 | 73 | 14.738 | 0.67242 | 15.5804 |  |  |  |  | 0.74 | 14.9385 | 0.14788 |  |  |  | 70.5
11:17 | 3941 | 72 | 274.6 | 10.3 | 74 | 14.6367 | 0.67242 | 15.6029 |  |  |  |  | 0.75 | 15.1323 | 0.15035 |  | 0.302 |  | 72
11:17 | 3930 | 75 | 274.6 | 10.3 | 75 | 14.9385 | 0.67242 | 15.6238 |  |  |  |  | 0.76 | 15.1323 | 0.15132 |  |  |  | 73
11:17 | 3930 | 77 | 274.3 | 10.3 | 76 | 15.1323 | 0.67279 | 15.6431 |  |  |  |  | 0.77 | 15.3275 | 0.1523 |  | 0.3059 |  | 73
11:17 | 3930 | 77 | 274.3 | 10.3 | 77 | 15.1323 | 0.67279 | 15.6609 |  |  |  |  | 0.78 | 15.3275 | 0.15328 |  |  |  | 74
11:17 | 3930 | 79 | 274.3 | 10.3 | 78 | 15.3275 | 0.67279 | 15.6772 |  |  |  |  | 0.79 | 16.2672 | 0.15797 |  | 0.32221 |  | 74
11:17 | 3933 | 79 | 274.3 | 10.3 | 79 | 15.3275 | 0.67279 | 15.6919 |  |  |  |  | 0.8 | 16.2672 | 0.16267 |  |  |  | 79
11:17 | 3936 | 89 | 274.2 | 10.3 | 80 | 16.2672 | 0.67291 | 15.7052 |  |  |  |  | 0.81 | 15.8051 | 0.16036 |  | 0.31734 |  | 79
11:17 | 3928 | 89 | 274.2 | 10.3 | 81 | 16.2672 | 0.67291 | 15.717 |  |  |  |  | 0.82 | 15.7137 | 0.15759 |  |  |  | 77.5
11:17 | 3916 | 84 | 274.3 | 10.3 | 82 | 15.8051 | 0.67279 | 15.7274 |  |  |  |  | 0.83 | 15.4271 | 0.1557 |  | 0.30853 |  | 77
11:17 | 3916 | 83 | 274.5 | 10.3 | 83 | 15.7137 | 0.67255 | 15.7364 |  |  |  |  | 0.84 | 15.1364 | 0.15282 |  |  |  | 76.5
11:17 | 3926 | 80 | 274.5 | 10.3 | 84 | 15.4271 | 0.67255 | 15.744 |  |  |  |  | 0.85 | 15.2344 | 0.15185 |  | 0.30501 |  | 77
11:17 | 3926 | 77 | 274.6 | 10.3 | 85 | 15.1364 | 0.67242 | 15.7503 |  |  |  |  | 0.86 | 15.4285 | 0.15331 |  |  |  | 77.5
11:17 | 3933 | 78 | 274.6 | 10.3 | 86 | 15.2344 | 0.67242 | 15.7553 |  |  |  |  | 0.87 | 15.4285 | 0.15428 |  | 0.30728 |  | 79
11:17 | 3934 | 80 | 274.6 | 10.3 | 87 | 15.4285 | 0.67242 | 15.7589 |  |  |  |  | 0.88 | 15.0406 | 0.15235 |  |  |  | 79
11:17 | 3940 | 80 | 274.6 | 10.3 | 88 | 15.4285 | 0.67242 | 15.7613 |  |  |  |  | 0.89 | 15.0433 | 0.15042 |  | 0.30052 |  | 78.5
11:17 | 3945 | 76 | 274.8 | 10.3 | 89 | 15.0406 | 0.67218 | 15.7625 |  |  |  |  | 0.9 | 14.9426 | 0.14993 |  |  |  | 78.5
11:17 | 3950 | 76 | 275 | 10.3 | 90 | 15.0433 | 0.67193 | 15.7625 |  |  |  |  | 0.91 | 14.9413 | 0.14942 |  | 0.29883 |  | 78.5
11:17 | 3957 | 75 | 274.9 | 10.3 | 91 | 14.9426 | 0.67205 | 15.7612 |  |  |  |  | 0.92 | 14.9413 | 0.14941 |  |  |  | 78.5
11:17 | 3957 | 75 | 274.8 | 10.3 | 92 | 14.9413 | 0.67218 | 15.7589 |  |  |  |  | 0.93 | 15.0392 | 0.1499 |  | 0.30079 |  | 79
11:17 | 3961 | 75 | 274.8 | 10.3 | 93 | 14.9413 | 0.67218 | 15.7553 |  |  |  |  | 0.94 | 15.1378 | 0.15088 |  |  |  | 80
11:17 | 3961 | 76 | 274.7 | 10.3 | 94 | 15.0392 | 0.6723 | 15.7507 |  |  |  |  | 0.95 | 15.5274 | 0.15333 |  | 0.30925 |  | 80.5
11:17 | 3961 | 77 | 274.7 | 10.3 | 95 | 15.1378 | 0.6723 | 15.745 |  |  |  |  | 0.96 | 15.5274 | 0.15527 |  |  |  | 82.5
11:17 | 3960 | 81 | 274.8 | 10.3 | 96 | 15.5274 | 0.67218 | 15.7383 |  |  |  |  | 0.97 | 15.3359 | 0.15432 |  | 0.30736 |  | 82.5
11:17 | 3960 | 81 | 274.8 | 10.3 | 97 | 15.5274 | 0.67218 | 15.7305 |  |  |  |  | 0.98 | 15.3359 | 0.15336 |  |  |  | 78
11:17 | 3960 | 79 | 274.9 | 10.3 | 98 | 15.3359 | 0.67205 | 15.7217 |  |  |  |  | 0.99 | 15.5303 | 0.15433 |  | 0.31028 |  | 78
11:17 | 3964 | 79 | 274.9 | 10.3 | 99 | 15.3359 | 0.67205 | 15.712 |  |  |  |  | 1 | 15.6273 | 0.15579 |  |  |  | 75
11:17 | 3971 | 81 | 275 | 10.3 | 100 | 15.5303 | 0.67193 | 15.7013 |  |  |  |  | 0 | 15.3387 | -15.483 |  | -15.2012 |  | 75
11:17 | 3970 | 82 | 275.1 | 10.3 | 101 | 15.6273 | 0.67181 | 15.6897 |  |  |  |  | 0.01 | 15.1461 | 0.15242 |  |  |  | 73.5
11:17 | 3967 | 79 | 275.1 | 10.3 | 102 | 15.3387 | 0.67181 | 15.6772 |  |  |  |  | 0.02 | 15.1461 | 0.15146 |  | 0.30291 |  | 73
11:17 | 3967 | 77 | 275.3 | 10.3 | 103 | 15.1461 | 0.67156 | 15.6639 |  |  |  |  | 0.03 | 15.1419 | 0.15144 |  |  |  | 74.5
11:17 | 3968 | 77 | 275.3 | 10.3 | 104 | 15.1461 | 0.67156 | 15.6497 |  |  |  |  | 0.04 | 15.1406 | 0.15141 |  | 0.30281 |  | 76.5
11:17 | 3969 | 77 | 275 | 10.3 | 105 | 15.1419 | 0.67193 | 15.6347 |  |  |  |  | 0.05 | 15.1392 | 0.1514 |  |  |  | 76.5
11:17 | 3962 | 77 | 274.9 | 10.3 | 106 | 15.1406 | 0.67205 | 15.6189 |  |  |  |  | 0.06 | 15.1378 | 0.15138 |  | 0.30277 |  | 79
11:17 | 3956 | 77 | 274.8 | 10.3 | 107 | 15.1392 | 0.67218 | 15.6023 |  |  |  |  | 0.07 | 15.1392 | 0.15138 |  |  |  | 79.5
11:17 | 3951 | 77 | 274.7 | 10.3 | 108 | 15.1378 | 0.6723 | 15.585 |  |  |  |  | 0.08 | 15.1406 | 0.1514 |  | 0.30281 |  | 79.5
11:17 | 3940 | 77 | 274.8 | 10.3 | 109 | 15.1392 | 0.67218 | 15.567 |  |  |  |  | 0.09 | 15.1406 | 0.15141 |  |  |  | 79.5
11:17 | 3940 | 77 | 274.9 | 10.3 | 110 | 15.1406 | 0.67205 | 15.5484 |  |  |  |  | 0.1 | 15.1433 | 0.15142 |  | 0.3022 |  | 79
11:17 | 3927 | 77 | 274.9 | 10.3 | 111 | 15.1406 | 0.67205 | 15.5291 |  |  |  |  | 0.11 | 14.9454 | 0.15044 |  |  |  | 78.5
11:17 | 3927 | 77 | 275.1 | 10.3 | 112 | 15.1433 | 0.67181 | 15.5091 |  |  |  |  | 0.12 | 14.5414 | 0.14743 |  | 0.29217 |  | 77.5
11:17 | 3927 | 75 | 275.1 | 10.4 | 113 | 14.9454 | 0.67181 | 15.4886 |  |  |  |  | 0.13 | 14.5414 | 0.14541 |  |  |  | 75.5
11:17 | 3927 | 71 | 275.1 | 10.4 | 114 | 14.5414 | 0.67181 | 15.4675 |  |  |  |  | 0.14 | 14.9454 | 0.14743 |  | 0.29756 |  | 75.5
11:17 | 3932 | 71 | 275.1 | 10.3 | 115 | 14.5414 | 0.67181 | 15.4458 |  |  |  |  | 0.15 | 14.944 | 0.14945 |  |  |  | 75.5
11:17 | 3936 | 75 | 275.1 | 10.3 | 116 | 14.9454 | 0.67181 | 15.4236 |  |  |  |  | 0.16 | 14.8454 | 0.14895 |  | 0.29725 |  | 75.5
11:17 | 3940 | 75 | 275 | 10.3 | 117 | 14.944 | 0.67193 | 15.401 |  |  |  |  | 0.17 | 14.8495 | 0.14847 |  |  |  | 72.5
11:17 | 3948 | 74 | 275.1 | 10.3 | 118 | 14.8454 | 0.67181 | 15.3779 |  |  |  |  | 0.18 | 15.1475 | 0.14998 |  | 0.30262 |  | 72
11:17 | 3949 | 74 | 275.4 | 10.3 | 119 | 14.8495 | 0.67144 | 15.3543 |  |  |  |  | 0.19 | 15.3457 | 0.15247 |  |  |  | 73.5
11:17 | 3959 | 77 | 275.4 | 10.3 | 120 | 15.1475 | 0.67144 | 15.3303 |  |  |  |  | 0.2 | 15.2483 | 0.15297 |  | 0.30463 |  | 74.5
11:17 | 3959 | 79 | 275.6 | 10.3 | 121 | 15.3457 | 0.6712 | 15.3059 |  |  |  |  | 0.21 | 15.0502 | 0.15149 |  |  |  | 74.5
11:17 | 3963 | 78 | 275.6 | 10.3 | 122 | 15.2483 | 0.6712 | 15.2812 |  |  |  |  | 0.22 | 15.0502 | 0.1505 |  | 0.30034 |  | 74
11:17 | 3965 | 76 | 275.5 | 10.3 | 123 | 15.0502 | 0.67132 | 15.2562 |  |  |  |  | 0.23 | 14.8508 | 0.1495 |  |  |  | 74
11:17 | 3967 | 76 | 275.5 | 10.3 | 124 | 15.0502 | 0.67132 | 15.2308 |  |  |  |  | 0.24 | 14.8495 | 0.1485 |  | 0.29666 |  | 74.5
11:17 | 3970 | 74 | 275.5 | 10.3 | 125 | 14.8508 | 0.67132 | 15.2052 |  |  |  |  | 0.25 | 14.7488 | 0.14799 |  |  |  | 74.5
11:17 | 3972 | 74 | 275.4 | 10.3 | 126 | 14.8495 | 0.67144 | 15.1793 |  |  |  |  | 0.26 | 14.6461 | 0.14697 |  | 0.2946 |  | 71.5
11:17 | 3977 | 73 | 275.4 | 10.3 | 127 | 14.7488 | 0.67144 | 15.1532 |  |  |  |  | 0.27 | 15.0474 | 0.14847 |  |  |  | 70.5
11:17 | 3977 | 72 | 275.3 | 10.3 | 128 | 14.6461 | 0.67156 | 15.1268 |  |  |  |  | 0.28 | 15.4341 | 0.15241 |  | 0.30771 |  | 72
11:17 | 3970 | 76 | 275.3 | 10.3 | 129 | 15.0474 | 0.67156 | 15.1004 |  |  |  |  | 0.29 | 15.5303 | 0.15482 |  |  |  | 73.5
11:17 | 3970 | 80 | 275 | 10.3 | 130 | 15.4341 | 0.67193 | 15.0737 |  |  |  |  | 0.3 | 15.7208 | 0.15626 |  | 0.31378 |  | 73.5
11:17 | 3960 | 81 | 275 | 10.3 | 131 | 15.5303 | 0.67193 | 15.047 |  |  |  |  | 0.31 | 15.7208 | 0.15721 |  |  |  | 74
11:17 | 3955 | 83 | 275 | 10.3 | 132 | 15.7208 | 0.67193 | 15.0201 |  |  |  |  | 0.32 | 15.4355 | 0.15578 |  | 0.30967 |  | 74
11:17 | 3949 | 83 | 275 | 10.3 | 133 | 15.7208 | 0.67193 | 14.9932 |  |  |  |  | 0.33 | 15.4369 | 0.15436 |  |  |  | 71
11:17 | 3944 | 80 | 275.1 | 10.3 | 134 | 15.4355 | 0.67181 | 14.9663 |  |  |  |  | 0.34 | 15.2427 | 0.1534 |  | 0.30549 |  | 71
11:17 | 3939 | 80 | 275.2 | 10.3 | 135 | 15.4369 | 0.67169 | 14.9393 |  |  |  |  | 0.35 | 15.2399 | 0.15241 |  |  |  | 70
11:17 | 3925 | 78 | 275.2 | 10.3 | 136 | 15.2427 | 0.67169 | 14.9124 |  |  |  |  | 0.36 | 14.944 | 0.15092 |  | 0.29886 |  | 70
11:17 | 3925 | 78 | 275 | 10.3 | 137 | 15.2399 | 0.67193 | 14.8855 |  |  |  |  | 0.37 | 14.6421 | 0.14793 |  |  |  | 70
11:17 | 3928 | 75 | 275 | 10.3 | 138 | 14.944 | 0.67193 | 14.8586 |  |  |  |  | 0.38 | 14.6421 | 0.14642 |  | 0.29285 |  | 69.5
11:17 | 3928 | 72 | 275 | 10.3 | 139 | 14.6421 | 0.67193 | 14.8319 |  |  |  |  | 0.39 | 14.6434 | 0.14643 |  |  |  | 70.5
11:17 | 3934 | 72 | 275 | 10.3 | 140 | 14.6421 | 0.67193 | 14.8053 |  |  |  |  | 0.4 | 14.6434 | 0.14643 |  | 0.2915 |  | 72.5
11:17 | 3937 | 72 | 275.1 | 10.3 | 141 | 14.6434 | 0.67181 | 14.7788 |  |  |  |  | 0.41 | 14.2321 | 0.14438 |  |  |  | 72.5
11:17 | 3937 | 72 | 275.1 | 10.3 | 142 | 14.6434 | 0.67181 | 14.7525 |  |  |  |  | 0.42 | 14.2334 | 0.14233 |  | 0.2857 |  | 71.5
11:17 | 3937 | 68 | 275.2 | 10.3 | 143 | 14.2321 | 0.67169 | 14.7264 |  |  |  |  | 0.43 | 14.544 | 0.14389 |  |  |  | 71.5
11:17 | 3936 | 68 | 275.3 | 10.3 | 144 | 14.2334 | 0.67156 | 14.7006 |  |  |  |  | 0.44 | 14.544 | 0.14544 |  | 0.29054 |  | 74.5
11:17 | 3934 | 71 | 275.3 | 10.3 | 145 | 14.544 | 0.67156 | 14.675 |  |  |  |  | 0.45 | 14.4412 | 0.14493 |  |  |  | 75
11:17 | 3934 | 71 | 275.3 | 10.3 | 146 | 14.544 | 0.67156 | 14.6496 |  |  |  |  | 0.46 | 14.4439 | 0.14443 |  | 0.28852 |  | 74
11:17 | 3921 | 70 | 275.3 | 10.3 | 147 | 14.4412 | 0.67156 | 14.6246 |  |  |  |  | 0.47 | 14.3403 | 0.14392 |  |  |  | 74
11:17 | 3921 | 70 | 275.5 | 10.3 | 148 | 14.4439 | 0.67132 | 14.5999 |  |  |  |  | 0.48 | 13.8122 | 0.14076 |  | 0.278 |  | 73
11:17 | 3905 | 69 | 275.5 | 10.3 | 149 | 14.3403 | 0.67132 | 14.5756 |  |  |  |  | 0.49 | 13.8122 | 0.13812 |  |  |  | 69.5
11:17 | 3896 | 64 | 275.6 | 10.3 | 150 | 13.8122 | 0.6712 | 14.5516 |  |  |  |  | 0.5 | 13.9184 | 0.13865 |  | 0.27801 |  | 69.5
11:17 | 3901 | 64 | 275.6 | 10.3 | 151 | 13.8122 | 0.6712 | 14.5281 |  |  |  |  | 0.51 | 13.9172 | 0.13918 |  |  |  | 73
11:17 | 3906 | 65 | 275.5 | 10.3 | 152 | 13.9184 | 0.67132 | 14.505 |  |  |  |  | 0.52 | 14.339 | 0.14128 |  | 0.28606 |  | 73.5
11:17 | 3908 | 65 | 275.4 | 10.3 | 153 | 13.9172 | 0.67144 | 14.4824 |  |  |  |  | 0.53 | 14.544 | 0.14442 |  |  |  | 75
11:17 | 3915 | 69 | 275.4 | 10.3 | 154 | 14.339 | 0.67144 | 14.4603 |  |  |  |  | 0.54 | 15.0474 | 0.14796 |  | 0.30055 |  | 75.5
11:17 | 3915 | 71 | 275.3 | 10.3 | 155 | 14.544 | 0.67156 | 14.4387 |  |  |  |  | 0.55 | 15.4313 | 0.15239 |  |  |  | 75.5
11:17 | 3924 | 76 | 275.3 | 10.3 | 156 | 15.0474 | 0.67156 | 14.4176 |  |  |  |  | 0.56 | 15.5274 | 0.15479 |  | 0.31212 |  | 74
11:17 | 3924 | 80 | 274.8 | 10.3 | 157 | 15.4313 | 0.67218 | 14.3972 |  |  |  |  | 0.57 | 16.0952 | 0.15811 |  |  |  | 73.5
11:17 | 3915 | 81 | 274.8 | 10.3 | 158 | 15.5274 | 0.67218 | 14.3773 |  |  |  |  | 0.58 | 16.0966 | 0.16096 |  | 0.32068 |  | 74
11:17 | 3911 | 87 | 275 | 10.3 | 159 | 16.0952 | 0.67193 | 14.358 |  |  |  |  | 0.59 | 15.7237 | 0.1591 |  |  |  | 74
11:17 | 3906 | 87 | 275.1 | 10.3 | 160 | 16.0966 | 0.67181 | 14.3394 |  |  |  |  | 0.6 | 15.7237 | 0.15724 |  | 0.3132 |  | 69
11:17 | 3902 | 83 | 275.2 | 10.3 | 161 | 15.7237 | 0.67169 | 14.3215 |  |  |  |  | 0.61 | 15.3401 | 0.15532 |  |  |  | 69
11:17 | 3902 | 83 | 275.2 | 10.3 | 162 | 15.7237 | 0.67169 | 14.3043 |  |  |  |  | 0.62 | 15.1433 | 0.15242 |  | 0.30219 |  | 67.5
11:17 | 3902 | 79 | 275.2 | 10.3 | 163 | 15.3401 | 0.67169 | 14.2878 |  |  |  |  | 0.63 | 14.7447 | 0.14944 |  |  |  | 67
11:17 | 3903 | 77 | 275.1 | 10.3 | 164 | 15.1433 | 0.67181 | 14.2721 |  |  |  |  | 0.64 | 14.432 | 0.14588 |  | 0.28968 |  | 65.5
11:17 | 3914 | 73 | 275.1 | 10.3 | 165 | 14.7447 | 0.67181 | 14.2572 |  |  |  |  | 0.65 | 14.432 | 0.14432 |  |  |  | 64
11:17 | 3914 | 70 | 274.6 | 10.3 | 166 | 14.432 | 0.67242 | 14.2431 |  |  |  |  | 0.66 | 14.3299 | 0.14381 |  | 0.28694 |  | 64
11:17 | 3914 | 70 | 274.6 | 10.3 | 167 | 14.432 | 0.67242 | 14.2298 |  |  |  |  | 0.67 | 14.3299 | 0.1433 |  |  |  | 63.5
11:17 | 3914 | 69 | 274.7 | 10.3 | 168 | 14.3299 | 0.6723 | 14.2174 |  |  |  |  | 0.68 | 14.3272 | 0.14329 |  | 0.28655 |  | 63.5
11:17 | 3913 | 69 | 274.7 | 10.3 | 169 | 14.3299 | 0.6723 | 14.2059 |  |  |  |  | 0.69 | 14.3259 | 0.14327 |  |  |  | 65.5
11:17 | 3912 | 69 | 274.5 | 10.3 | 170 | 14.3272 | 0.67255 | 14.1953 |  |  |  |  | 0.7 | 14.2217 | 0.14274 |  | 0.28445 |  | 65.5
11:17 | 3910 | 69 | 274.4 | 10.3 | 171 | 14.3259 | 0.67267 | 14.1857 |  |  |  |  | 0.71 | 14.1207 | 0.14171 |  |  |  | 64.5
11:17 | 3899 | 68 | 274.4 | 10.3 | 172 | 14.2217 | 0.67267 | 14.177 |  |  |  |  | 0.72 | 14.0149 | 0.14068 |  | 0.27995 |  | 64
11:17 | 3899 | 67 | 274.7 | 10.3 | 173 | 14.1207 | 0.6723 | 14.1693 |  |  |  |  | 0.73 | 13.8034 | 0.13909 |  |  |  | 62.5
11:17 | 3885 | 66 | 274.7 | 10.3 | 174 | 14.0149 | 0.6723 | 14.1627 |  |  |  |  | 0.74 | 13.8034 | 0.13803 |  | 0.27571 |  | 60.5
11:17 | 3885 | 64 | 274.9 | 10.3 | 175 | 13.8034 | 0.67205 | 14.1571 |  |  |  |  | 0.75 | 13.6952 | 0.13749 |  |  |  | 60.5
11:17 | 3892 | 64 | 274.9 | 10.3 | 176 | 13.8034 | 0.67205 | 14.1526 |  |  |  |  | 0.76 | 13.6952 | 0.13695 |  | 0.27426 |  | 60
11:17 | 3898 | 63 | 274.9 | 10.3 | 177 | 13.6952 | 0.67205 | 14.1492 |  |  |  |  | 0.77 | 13.8034 | 0.13749 |  |  |  | 60
11:17 | 3902 | 63 | 274.9 | 10.3 | 178 | 13.6952 | 0.67205 | 14.1469 |  |  |  |  | 0.78 | 13.8034 | 0.13803 |  | 0.27498 |  | 62
11:17 | 3906 | 64 | 274.9 | 10.3 | 179 | 13.8034 | 0.67205 | 14.1458 |  |  |  |  | 0.79 | 13.476 | 0.1364 |  |  |  | 62
11:17 | 3908 | 64 | 274.9 | 10.3 | 180 | 13.8034 | 0.67205 | 14.1459 |  |  |  |  | 0.8 | 13.2545 | 0.13365 |  | 0.26766 |  | 59.5
11:18 | 3924 | 61 | 274.9 | 10.3 | 181 | 13.476 | 0.67205 | 14.1472 |  |  |  |  | 0.81 | 13.8047 | 0.1353 |  |  |  | 57.5
11:18 | 3924 | 59 | 275 | 10.3 | 182 | 13.2545 | 0.67193 | 14.1497 |  |  |  |  | 0.82 | 14.3325 | 0.14069 |  | 0.28489 |  | 60.5
11:18 | 3921 | 64 | 275 | 10.3 | 183 | 13.8047 | 0.67193 | 14.1535 |  |  |  |  | 0.83 | 14.3325 | 0.14332 |  |  |  | 63
11:18 | 3921 | 69 | 274.9 | 10.3 | 184 | 14.3325 | 0.67205 | 14.1586 |  |  |  |  | 0.84 | 14.4373 | 0.14385 |  | 0.28806 |  | 62.5
11:18 | 3915 | 69 | 274.9 | 10.2 | 185 | 14.3325 | 0.67205 | 14.165 |  |  |  |  | 0.85 | 14.3364 | 0.14387 |  |  |  | 60
11:18 | 3912 | 70 | 275 | 10.2 | 186 | 14.4373 | 0.67193 | 14.1728 |  |  |  |  | 0.86 | 13.7001 | 0.14018 |  | 0.27613 |  | 59.5
11:18 | 3907 | 69 | 275.2 | 10.3 | 187 | 14.3364 | 0.67169 | 14.1819 |  |  |  |  | 0.87 | 13.7014 | 0.13701 |  |  |  | 56.5
11:18 | 3903 | 63 | 275.3 | 10.3 | 188 | 13.7001 | 0.67156 | 14.1925 |  |  |  |  | 0.88 | 13.8097 | 0.13756 |  | 0.27584 |  | 56.5
11:18 | 3903 | 63 | 275.4 | 10.3 | 189 | 13.7014 | 0.67144 | 14.2044 |  |  |  |  | 0.89 | 13.811 | 0.1381 |  |  |  | 56
11:18 | 3907 | 64 | 275.4 | 10.3 | 190 | 13.8097 | 0.67144 | 14.2179 |  |  |  |  | 0.9 | 14.131 | 0.13971 |  | 0.28226 |  | 55.5
11:18 | 3907 | 64 | 275.5 | 10.3 | 191 | 13.811 | 0.67132 | 14.2328 |  |  |  |  | 0.91 | 14.3442 | 0.14238 |  |  |  | 57
11:18 | 3918 | 67 | 275.5 | 10.3 | 192 | 14.131 | 0.67132 | 14.2492 |  |  |  |  | 0.92 | 14.3442 | 0.14344 |  | 0.28688 |  | 58.5
11:18 | 3918 | 69 | 275.8 | 10.3 | 193 | 14.3442 | 0.67095 | 14.2671 |  |  |  |  | 0.93 | 14.3442 | 0.14344 |  |  |  | 58
11:18 | 3922 | 69 | 275.8 | 10.3 | 194 | 14.3442 | 0.67095 | 14.2866 |  |  |  |  | 0.94 | 14.3442 | 0.14344 |  | 0.28583 |  | 55
11:18 | 3926 | 69 | 275.8 | 10.3 | 195 | 14.3442 | 0.67095 | 14.3077 |  |  |  |  | 0.95 | 14.0289 | 0.14187 |  |  |  | 55
11:18 | 3933 | 69 | 275.8 | 10.3 | 196 | 14.3442 | 0.67095 | 14.3304 |  |  |  |  | 0.96 | 14.0277 | 0.14028 |  | 0.28091 |  | 49.5
11:18 | 3941 | 66 | 275.8 | 10.3 | 197 | 14.0289 | 0.67095 | 14.3547 |  |  |  |  | 0.97 | 14.1335 | 0.14081 |  |  |  | 49
11:18 | 3941 | 66 | 275.7 | 10.3 | 198 | 14.0277 | 0.67108 | 14.3807 |  |  |  |  | 0.98 | 14.2334 | 0.14183 |  | 0.28363 |  | 50
11:18 | 3950 | 67 | 275.7 | 10.3 | 199 | 14.1335 | 0.67108 | 14.4084 |  |  |  |  | 0.99 | 14.0225 | 0.14128 |  |  |  | 50.5
11:18 | 3950 | 68 | 275.3 | 10.3 | 200 | 14.2334 | 0.67156 | 14.4378 |  |  |  |  | 1 | 13.8072 | 0.13915 |  |  |  | 49
11:18 | 3973 | 66 | 275.3 | 10.3 | 201 | 14.0225 | 0.67156 | 14.469 | [10 empty] | 47
11:18 | 3973 | 64 | 275.2 | 10.3 | 202 | 13.8072 | 0.67169 | 14.5019 | [10 empty] | 47
11:18 | 3975 | 64 | 275.2 | 10.3 | 203 | 13.8072 | 0.67169 | 14.5367 | [10 empty] | 45.5
11:18 | 3976 | 64 | 275.1 | 10.3 | 204 | 13.8059 | 0.67181 | 14.5732 | [10 empty] | 45.5
11:18 | 3973 | 64 | 275 | 10.3 | 205 | 13.8047 | 0.67193 | 14.6117 | [10 empty] | 50.5
11:18 | 3969 | 66 | 275 | 10.3 | 206 | 14.0187 | 0.67193 | 14.652 | [10 empty] | 50.5
11:18 | 3968 | 66 | 275 | 10.3 | 207 | 14.0187 | 0.67193 | 14.6942 | [10 empty] | 51.5
11:18 | 3956 | 65 | 275 | 10.3 | 208 | 13.9121 | 0.67193 | 14.7383 | [10 empty] | 53
11:18 | 3956 | 65 | 275.2 | 10.3 | 209 | 13.9146 | 0.67169 | 14.7844 | [10 empty] | 52
11:18 | 3952 | 63 | 275.2 | 10.3 | 210 | 13.6989 | 0.67169 | 14.8325
11:18 | 3952 | 61 | 275.5 | 10.3 |  | 13.4834 | 0.67132
11:18 | 3962 | 61 | 275.5 | 10.4 |  | 13.4834 | 0.67132
11:18 | 3970 | 57 | 275.5 | 10.4 |  | 13.0338 | 0.67132
11:18 | 3978 | 57 | 275.4 | 10.4 |  | 13.0326 | 0.67144
11:18 | 3986 | 61 | 275.4 | 10.4 |  | 13.4822 | 0.67144
11:18 | 3985 | 61 | 275.4 | 10.4 |  | 13.4822 | 0.67144
11:18 | 3975 | 57 | 275.4 | 10.4 |  | 13.0326 | 0.67144
11:18 | 3975 | 53 | 275.3 | 10.4 |  | 12.5659 | 0.67156
11:18 | 3969 | 50 | 275.3 | 10.4 |  | 12.2051 | 0.67156
11:18 | 3969 | 47 | 275.4 | 10.4 |  | 11.8343 | 0.67144
11:18 | 3966 | 47 | 275.4 | 10.4 |  | 11.8343 | 0.67144
11:18 | 3964 | 44 | 275.3 | 10.4 |  | 11.4494 | 0.67156
11:18 | 3967 | 44 | 275.2 | 10.3 |  | 11.4483 | 0.67169
11:18 | 3970 | 41 | 275.3 | 10.3 |  | 11.0522 | 0.67156
11:18 | 3971 | 41 | 275.5 | 10.3 |  | 11.0542 | 0.67132
11:18 | 3973 | 41 | 275.5 | 10.3 |  | 11.0542 | 0.67132
11:18 | 3973 | 41 | 275 | 10.3 |  | 11.0491 | 0.67193
11:18 | 3962 | 38 | 275 | 10.3 |  | 10.6372 | 0.67193
11:18 | 3961 | 35 | 274.8 | 10.3 |  | 10.2068 | 0.67218
11:18 | 3959 | 35 | 274.8 | 10.3 |  | 10.2068 | 0.67218
11:18 | 3958 | 27 | 274.8 | 10.3 |  | 8.9648 | 0.67218
11:18 | 3962 | 27 | 274.9 | 10.3 |  | 8.9656 | 0.67205
11:18 | 3968 | 30 | 274.9 | 10.3 |  | 9.4506 | 0.67205
11:18 | 3969 | 30 | 275 | 10.3 |  | 9.4514 | 0.67193
11:18 | 3978 | 32 | 275 | 10.3 |  | 9.7614 | 0.67193
11:18 | 3978 | 33 | 275.2 | 10.3 |  | 9.9145 | 0.67169
11:18 | 3994 | 33 | 275.2 | 10.2 |  | 9.9145 | 0.67169
11:18 | 3996 | 32 | 275.4 | 10.2 |  | 9.7649 | 0.67144
11:18 | 4003 | 33 | 275.4 | 10.2 |  | 9.9163 | 0.67144
11:18 | 4010 | 41 | 275.6 | 10.2 |  | 11.0552 | 0.6712
11:18 | 4008 | 41 | 275.7 | 10.2 |  | 11.0562 | 0.67108
11:18 | 4006 | 47 | 275.7 | 10.2 |  | 11.8376 | 0.67108
11:18 | 4006 | 48 | 275.7 | 10.2 |  | 11.9628 | 0.67108
11:18 | 3995 | 47 | 275.7 | 10.2 |  | 11.8376 | 0.67108
11:18 | 3995 | 47 | 275.7 | 10.2 |  | 11.8376 | 0.67108
11:18 | 3988 | 48 | 275.7 | 10.3 |  | 11.9628 | 0.67108
11:18 | 3987 | 50 | 275.8 | 10.3 |  | 12.2106 | 0.67095
11:18 | 3980 | 50 | 275.8 | 10.3 |  | 12.2106 | 0.67095
11:18 | 3973 | 50 | 275.8 | 10.3 |  | 12.2106 | 0.67095
11:18 | 3975 | 50 | 275.8 | 10.3 |  | 12.2106 | 0.67095
11:18 | 3979 | 56 | 275.8 | 10.3 |  | 12.9225 | 0.67095
11:18 | 3979 | 57 | 276 | 10.3 |  | 13.0398 | 0.67071
11:18 | 3971 | 57 | 276 | 10.3 |  | 13.0398 | 0.67071
11:18 | 3971 | 56 | 275.6 | 10.3 |  | 12.9202 | 0.6712
11:18 | 3965 | 58 | 275.6 | 10.3 |  | 13.1488 | 0.6712
11:18 | 3964 | 60 | 275.7 | 10.3 |  | 13.3748 | 0.67108
11:18 | 3955 | 60 | 275.7 | 10.3 |  | 13.3748 | 0.67108
11:18 | 3946 | 57 | 275.7 | 10.3 |  | 13.0362 | 0.67108
11:18 | 3937 | 57 | 275.8 | 10.3 |  | 13.0374 | 0.67095
11:18 | 3923 | 57 | 275.8 | 10.3 |  | 13.0374 | 0.67095
11:18 | 3922 | 57 | 275.9 | 10.3 |  | 13.0386 | 0.67083
11:18 | 3912 | 59 | 275.9 | 10.3 |  | 13.2653 | 0.67083
11:18 | 3912 | 61 | 275.8 | 10.3 |  | 13.4871 | 0.67095
11:18 | 3897 | 61 | 275.8 | 10.2 |  | 13.4871 | 0.67095
11:18 | 3894 | 62 | 276.1 | 10.2 |  | 13.6009 | 0.67059
11:18 | 3893 | 62 | 276.2 | 10.2 |  | 13.6021 | 0.67046
11:18 | 3892 | 58 | 276.3 | 10.2 |  | 13.1572 | 0.67034
11:18 | 3893 | 58 | 276.3 | 10.2 |  | 13.1572 | 0.67034
11:18 | 3894 | 58 | 276.3 | 10.2 |  | 13.1572 | 0.67034
11:18 | 3894 | 58 | 276.3 | 10.2 |  | 13.1572 | 0.67034
11:18 | 3896 | 58 | 276.3 | 10.2 |  | 13.1572 | 0.67034
11:18 | 3896 | 57 | 276.3 | 10.2 |  | 13.0433 | 0.67034
11:18 | 3910 | 56 | 276.3 | 10.2 |  | 12.9284 | 0.67034
11:18 | 3913 | 55 | 276.4 | 10.2 |  | 12.8136 | 0.67022
11:18 | 3921 | 55 | 276.4 | 10.2 |  | 12.8136 | 0.67022
11:18 | 3929 | 61 | 276.6 | 10.2 |  | 13.4969 | 0.66998
11:18 | 3928 | 61 | 276.7 | 10.3 |  | 13.4981 | 0.66986
11:18 | 3926 | 66 | 276.7 | 10.3 |  | 14.0404 | 0.66986
11:18 | 3926 | 68 | 276.6 | 10.3 |  | 14.2503 | 0.66998
11:18 | 3926 | 75 | 276.6 | 10.3 |  | 14.9658 | 0.66998
11:18 | 3926 | 80 | 276.6 | 10.3 |  | 15.4566 | 0.66998
11:18 | 3927 | 81 | 276.6 | 10.3 |  | 15.5529 | 0.66998
11:18 | 3927 | 82 | 276.5 | 10.3 |  | 15.6472 | 0.6701
11:18 | 3930 | 81 | 276.5 | 10.3 |  | 15.5515 | 0.6701
11:18 | 3933 | 75 | 276.3 | 10.3 |  | 14.9617 | 0.67034
11:18 | 3939 | 75 | 276 | 10.3 |  | 14.9576 | 0.67071
11:18 | 3954 | 77 | 275.9 | 10.3 |  | 15.1544 | 0.67083
11:18 | 3954 | 78 | 275.7 | 10.3 |  | 15.2497 | 0.67108
11:18 | 3958 | 78 | 275.7 | 10.3 |  | 15.2497 | 0.67108
11:18 | 3958 | 79 | 275.4 | 10.3 |  | 15.3429 | 0.67144
11:18 | 3955 | 78 | 275.4 | 10.3 |  | 15.2455 | 0.67144
11:18 | 3954 | 75 | 275.7 | 10.3 |  | 14.9535 | 0.67108
11:18 | 3948 | 75 | 275.8 | 10.3 |  | 14.9549 | 0.67095
11:18 | 3941 | 73 | 275.8 | 10.3 |  | 14.7542 | 0.67095
11:18 | 3937 | 73 | 275.8 | 10.3 |  | 14.7542 | 0.67095
11:18 | 3929 | 69 | 275.9 | 10.3 |  | 14.3455 | 0.67083
11:18 | 3929 | 67 | 276.2 | 10.3 |  | 14.14 | 0.67046
11:18 | 3919 | 65 | 276.2 | 10.3 |  | 13.9273 | 0.67046
11:18 | 3919 | 62 | 276.2 | 10.3 |  | 13.6021 | 0.67046
11:18 | 3913 | 62 | 276.2 | 10.3 |  | 13.6021 | 0.67046
11:18 | 3911 | 62 | 276.5 | 10.3 |  | 13.6058 | 0.6701
11:18 | 3903 | 62 | 276.6 | 10.3 |  | 13.6071 | 0.66998
11:18 | 3896 | 65 | 276.5 | 10.3 |  | 13.9311 | 0.6701
11:18 | 3890 | 65 | 276.4 | 10.3 |  | 13.9299 | 0.67022
11:18 | 3875 | 66 | 276.3 | 10.3 |  | 14.0353 | 0.67034
11:18 | 3875 | 67 | 275.9 | 10.3 |  | 14.1361 | 0.67083
11:18 | 3868 | 68 | 275.9 | 10.3 |  | 14.2412 | 0.67083
11:18 | 3868 | 69 | 275.7 | 10.3 |  | 14.3429 | 0.67108
11:18 | 3868 | 70 | 275.7 | 10.3 |  | 14.4465 | 0.67108
11:18 | 3868 | 75 | 275.5 | 10.3 |  | 14.9508 | 0.67132
11:18 | 3875 | 75 | 275.4 | 10.3 |  | 14.9494 | 0.67144
11:18 | 3882 | 72 | 275.3 | 10.3 |  | 14.6461 | 0.67156
11:18 | 3885 | 72 | 275.2 | 10.3 |  | 14.6447 | 0.67169
11:18 | 3893 | 71 | 275.1 | 10.3 |  | 14.5414 | 0.67181
11:18 | 3893 | 70 | 274.9 | 10.3 |  | 14.436 | 0.67205
11:18 | 3898 | 70 | 275 | 10.4 |  | 14.4373 | 0.67193
11:18 | 3898 | 70 | 275.5 | 10.4 |  | 14.4439 | 0.67132
11:18 | 3897 | 71 | 275.5 | 10.4 |  | 14.5467 | 0.67132
11:18 | 3897 | 76 | 275.4 | 10.4 |  | 15.0488 | 0.67144
11:18 | 3898 | 76 | 275.3 | 10.3 |  | 15.0474 | 0.67156
11:18 | 3899 | 80 | 275.3 | 10.3 |  | 15.4383 | 0.67156
11:18 | 3900 | 80 | 275.3 | 10.3 |  | 15.4383 | 0.67156
11:18 | 3902 | 80 | 275.3 | 10.3 |  | 15.4383 | 0.67156
11:18 | 3902 | 80 | 275 | 10.3 |  | 15.4341 | 0.67193
11:18 | 3904 | 81 | 275 | 10.3 |  | 15.5303 | 0.67193
11:18 | 3904 | 82 | 274.8 | 10.3 |  | 15.623 | 0.67218
11:18 | 3906 | 82 | 274.8 | 10.3 |  | 15.623 | 0.67218
11:18 | 3906 | 82 | 274.9 | 10.3 |  | 15.6244 | 0.67205
11:18 | 3908 | 81 | 274.9 | 10.3 |  | 15.5288 | 0.67205
11:18 | 3909 | 76 | 275.1 | 10.3 |  | 15.0447 | 0.67181
11:18 | 3909 | 76 | 275.3 | 10.3 |  | 15.0474 | 0.67156
11:18 | 3912 | 72 | 275.3 | 10.3 |  | 14.6461 | 0.67156
11:18 | 3912 | 69 | 275.3 | 10.3 |  | 14.3377 | 0.67156
11:18 | 3923 | 68 | 275.3 | 10.3 |  | 14.2334 | 0.67156
11:18 | 3923 | 68 | 275.4 | 10.3 |  | 14.2347 | 0.67144
11:18 | 3926 | 69 | 275.4 | 10.3 |  | 14.339 | 0.67144
11:18 | 3927 | 77 | 275.5 | 10.3 |  | 15.1488 | 0.67132
11:18 | 3922 | 77 | 275.6 | 10.3 |  | 15.1502 | 0.6712
11:18 | 3917 | 84 | 275.4 | 10.3 |  | 15.821 | 0.67144
11:18 | 3915 | 84 | 275.3 | 10.3 |  | 15.8196 | 0.67156
11:18 | 3910 | 84 | 275.3 | 10.3 |  | 15.8196 | 0.67156
11:18 | 3910 | 84 | 275 | 10.3 |  | 15.8152 | 0.67193
11:18 | 3893 | 83 | 275 | 10.3 |  | 15.7208 | 0.67193
11:18 | 3893 | 82 | 275.1 | 10.3 |  | 15.6273 | 0.67181
11:18 | 3880 | 82 | 275.1 | 10.3 |  | 15.6273 | 0.67181
11:18 | 3871 | 81 | 274.8 | 10.3 |  | 15.5274 | 0.67218
11:18 | 3878 | 81 | 274.6 | 10.3 |  | 15.5246 | 0.67242
11:18 | 3885 | 78 | 274.6 | 10.3 |  | 15.2344 | 0.67242
11:18 | 3885 | 78 | 274.5 | 10.3 |  | 15.233 | 0.67255
11:18 | 3883 | 77 | 274.5 | 10.3 |  | 15.135 | 0.67255
11:18 | 3883 | 77 | 274.7 | 10.3 |  | 15.1378 | 0.6723
11:18 | 3881 | 73 | 274.7 | 10.3 |  | 14.7394 | 0.6723
11:18 | 3881 | 71 | 275 | 10.3 |  | 14.54 | 0.67193
11:18 | 3888 | 71 | 275 | 10.3 |  | 14.54 | 0.67193
11:18 | 3892 | 69 | 275.1 | 10.3 |  | 14.3351 | 0.67181
11:18 | 3892 | 69 | 275.2 | 10.2 |  | 14.3364 | 0.67169
11:18 | 3892 | 69 | 275.1 | 10.2 |  | 14.3351 | 0.67181
11:18 | 3894 | 69 | 275 | 10.2 |  | 14.3338 | 0.67193
11:18 | 3911 | 69 | 275 | 10.2 |  | 14.3338 | 0.67193
11:18 | 3912 | 69 | 274.8 | 10.2 |  | 14.3312 | 0.67218
11:18 | 3921 | 69 | 274.8 | 10.2 |  | 14.3312 | 0.67218
11:18 | 3921 | 69 | 274.5 | 10.2 |  | 14.3272 | 0.67255
11:18 | 3918 | 69 | 274.5 | 10.2 |  | 14.3272 | 0.67255
11:18 | 3915 | 69 | 274.7 | 10.2 |  | 14.3299 | 0.6723
11:18 | 3914 | 69 | 274.8 | 10.3 |  | 14.3312 | 0.67218
11:18 | 3914 | 70 | 274.7 | 10.3 |  | 14.4333 | 0.6723
11:18 | 3913 | 70 | 274.6 | 10.2 |  | 14.432 | 0.67242
11:18 | 3907 | 70 | 274.6 | 10.2 |  | 14.432 | 0.67242
11:18 | 3907 | 70 | 274.6 | 10.2 |  | 14.432 | 0.67242
11:18 | 3911 | 70 | 274.6 | 10.2 |  | 14.432 | 0.67242
11:18 | 3911 | 70 | 274.8 | 10.2 |  | 14.4346 | 0.67218
11:18 | 3925 | 70 | 274.8 | 10.2 |  | 14.4346 | 0.67218
11:18 | 3938 | 69 | 274.9 | 10.2 |  | 14.3325 | 0.67205
11:18 | 3947 | 69 | 275 | 10.2 |  | 14.3338 | 0.67193
11:18 | 3956 | 72 | 274.9 | 10.2 |  | 14.6407 | 0.67205
11:18 | 3957 | 72 | 274.7 | 10.2 |  | 14.6381 | 0.6723
11:18 | 3979 | 74 | 274.7 | 10.2 |  | 14.84 | 0.6723
11:18 | 3979 | 75 | 274.7 | 10.2 |  | 14.9399 | 0.6723
11:18 | 3989 | 77 | 274.7 | 10.2 |  | 15.1378 | 0.6723
11:18 | 3989 | 78 | 274.8 | 10.2 |  | 15.2372 | 0.67218
11:18 | 3982 | 79 | 274.8 | 10.2 |  | 15.3345 | 0.67218
11:18 | 3976 | 80 | 274.9 | 10.3 |  | 15.4327 | 0.67205
11:18 | 3975 | 80 | 275 | 10.3 |  | 15.4341 | 0.67193
11:18 | 3974 | 75 | 275 | 10.3 |  | 14.944 | 0.67193
11:18 | 3974 | 75 | 274.9 | 10.3 |  | 14.9426 | 0.67205
11:18 | 3978 | 77 | 274.9 | 10.3 |  | 15.1406 | 0.67205
11:18 | 3978 | 79 | 274.8 | 10.3 |  | 15.3345 | 0.67218
11:18 | 3970 | 79 | 274.8 | 10.3 |  | 15.3345 | 0.67218
11:18 | 3970 | 80 | 275 | 10.3 |  | 15.4341 | 0.67193
11:18 | 3968 | 80 | 275 | 10.3 |  | 15.4341 | 0.67193
11:18 | 3967 | 83 | 275.1 | 10.3 |  | 15.7223 | 0.67181
11:18 | 3966 | 83 | 275.3 | 10.3 |  | 15.7251 | 0.67156
11:18 | 3964 | 85 | 275.2 | 10.3 |  | 15.912 | 0.67169
11:18 | 3963 | 85 | 275.2 | 10.3 |  | 15.912 | 0.67169
11:18 | 3956 | 83 | 275.2 | 10.3 |  | 15.7237 | 0.67169
11:18 | 3956 | 81 | 275.6 | 10.3 |  | 15.5388 | 0.6712
11:18 | 3963 | 82 | 275.6 | 10.3 |  | 15.6344 | 0.6712
11:18 | 3963 | 82 | 275.8 | 10.3 |  | 15.6372 | 0.67095
11:18 | 3966 | 83 | 275.8 | 10.3 |  | 15.7323 | 0.67095
11:18 | 3968 | 85 | 275.8 | 10.3 |  | 15.9207 | 0.67095
11:18 | 3964 | 85 | 275.7 | 10.2 |  | 15.9193 | 0.67108
11:18 | 3958 | 79 | 275.8 | 10.2 |  | 15.3485 | 0.67095
11:18 | 3958 | 78 | 275.8 | 10.2 |  | 15.2511 | 0.67095
11:18 | 3956 | 78 | 275.8 | 10.2 |  | 15.2511 | 0.67095
11:18 | 3956 | 78 | 275.9 | 10.2 |  | 15.2525 | 0.67083
11:18 | 3958 | 79 | 275.9 | 10.2 |  | 15.3499 | 0.67083
11:18 | 3958 | 80 | 275.8 | 10.2 |  | 15.4454 | 0.67095
11:18 | 3963 | 80 | 275.7 | 10.2 |  | 15.4439 | 0.67108
11:18 | 3967 | 73 | 275.8 | 10.2 |  | 14.7542 | 0.67095
11:18 | 3963 | 73 | 275.9 | 10.2 |  | 14.7555 | 0.67083
11:18 | 3956 | 68 | 275.8 | 10.2 |  | 14.2399 | 0.67095
11:18 | 3956 | 67 | 275.6 | 10.3 |  | 14.1322 | 0.6712
11:18 | 3956 | 66 | 275.6 | 10.3 |  | 14.0264 | 0.6712
11:18 | 3956 | 65 | 275.9 | 10.2 |  | 13.9235 | 0.67083
11:18 | 3951 | 62 | 275.9 | 10.2 |  | 13.5984 | 0.67083
11:18 | 3951 | 59 | 276.3 | 10.2 |  | 13.2702 | 0.67034
11:18 | 3949 | 59 | 276.3 | 10.2 |  | 13.2702 | 0.67034
11:18 | 3947 | 61 | 276.3 | 10.2 |  | 13.4932 | 0.67034
11:18 | 3948 | 61 | 276.3 | 10.2 |  | 13.4932 | 0.67034
11:18 | 3949 | 61 | 276 | 10.2 |  | 13.4895 | 0.67071
11:18 | 3949 | 61 | 275.6 | 10.3 |  | 13.4846 | 0.6712
11:18 | 3962 | 61 | 275.6 | 10.3 |  | 13.4846 | 0.6712
11:18 | 3962 | 62 | 275.5 | 10.3 |  | 13.5935 | 0.67132
11:18 | 3959 | 60 | 275.5 | 10.3 |  | 13.3724 | 0.67132
11:18 | 3959 | 57 | 275.4 | 10.3 |  | 13.0326 | 0.67144
11:18 | 3961 | 57 | 275.3 | 10.3 |  | 13.0314 | 0.67156
11:18 | 3964 | 49 | 275.4 | 10.3 |  | 12.0835 | 0.67144
11:18 | 3962 | 49 | 275.5 | 10.3 |  | 12.0846 | 0.67132
11:18 | 3958 | 42 | 275.5 | 10.3 |  | 11.1882 | 0.67132
11:18 | 3958 | 41 | 275.6 | 10.3 |  | 11.0552 | 0.6712
11:18 | 3944 | 38 | 275.5 | 10.3 |  | 10.6421 | 0.67132
11:18 | 3944 | 36 | 275.2 | 10.3 |  | 10.3554 | 0.67169
11:18 | 3960 | 35 | 275.2 | 10.3 |  | 10.2106 | 0.67169
11:18 | 3962 | 33 | 275.1 | 10.3 |  | 9.9136 | 0.67181
11:18 | 3968 | 33 | 275 | 10.3 |  | 9.9127 | 0.67193

## P2
| Port | 2
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current
| Pa | Pa | Deg C | mA
Averages | 4015.6189 | 62.8707 | 271.6097 | 10.3443 | [11 empty] | 14.5911 |  | 14.3186
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current |  |  |  |  | a | b | n | h | xi | f(xi) | Aj
| Pa. | Pa | Deg C | mA |  | 13.3703 |  |  | 0 | 1 | 100 | 0.01 | 0 | 10.5925
[6 empty] | vel | dens | [5 empty] | 0.01 | 10.5906 | 0.10592 |  | 0.21182
11:20 | 4002 | 38 | 270.4 | 10.3 | 1 | 10.5925 | 0.67762 | 10.5305 |  |  |  |  | 0.02 | 10.5906 | 0.10591
11:20 | 4002 | 38 | 270.2 | 10.3 | 2 | 10.5906 | 0.67787 | 10.8309 |  |  |  |  | 0.03 | 10.8667 | 0.10729 |  | 0.21641
11:20 | 4006 | 38 | 270.2 | 10.3 | 3 | 10.5906 | 0.67787 | 11.1213 |  |  |  |  | 0.04 | 10.8667 | 0.10867
11:20 | 4009 | 40 | 270.3 | 10.3 | 4 | 10.8667 | 0.67774 | 11.4019 |  |  |  |  | 0.05 | 11.3971 | 0.11132 |  | 0.22617
11:20 | 4010 | 40 | 270.3 | 10.3 | 5 | 10.8667 | 0.67774 | 11.6729 |  |  |  |  | 0.06 | 11.396 | 0.11397
11:20 | 4010 | 44 | 270.3 | 10.3 | 6 | 11.3971 | 0.67774 | 11.9346 |  |  |  |  | 0.07 | 11.7781 | 0.11587 |  | 0.2351
11:20 | 4010 | 44 | 270.2 | 10.3 | 7 | 11.396 | 0.67787 | 12.1869 |  |  |  |  | 0.08 | 12.0228 | 0.119
11:20 | 4009 | 47 | 270.2 | 10.3 | 8 | 11.7781 | 0.67787 | 12.4303 |  |  |  |  | 0.09 | 12.2657 | 0.12144 |  | 0.2449
11:20 | 4009 | 49 | 269.9 | 10.3 | 9 | 12.0228 | 0.67824 | 12.6647 |  |  |  |  | 0.1 | 12.3831 | 0.12324
11:20 | 4004 | 51 | 269.9 | 10.3 | 10 | 12.2657 | 0.67824 | 12.8904 |  |  |  |  | 0.11 | 12.3831 | 0.12383 |  | 0.24961
11:20 | 4004 | 52 | 269.7 | 10.4 | 11 | 12.3831 | 0.67849 | 13.1076 |  |  |  |  | 0.12 | 12.9683 | 0.12676
11:20 | 4005 | 52 | 269.7 | 10.4 | 12 | 12.3831 | 0.67849 | 13.3164 |  |  |  |  | 0.13 | 12.9719 | 0.1297 |  | 0.26127
11:20 | 4005 | 57 | 270 | 10.4 | 13 | 12.9683 | 0.67812 | 13.517 |  |  |  |  | 0.14 | 13.5264 | 0.13249
11:20 | 4015 | 57 | 270.3 | 10.4 | 14 | 12.9719 | 0.67774 | 13.7096 |  |  |  |  | 0.15 | 13.5227 | 0.13525 |  | 0.27154
11:20 | 4025 | 62 | 270.1 | 10.4 | 15 | 13.5264 | 0.67799 | 13.8943 |  |  |  |  | 0.16 | 13.846 | 0.13684
11:20 | 4025 | 62 | 269.8 | 10.4 | 16 | 13.5227 | 0.67837 | 14.0712 |  |  |  |  | 0.17 | 14.1606 | 0.14003 |  | 0.28453
11:20 | 4032 | 65 | 269.8 | 10.4 | 17 | 13.846 | 0.67837 | 14.2407 |  |  |  |  | 0.18 | 14.8716 | 0.14516
11:20 | 4032 | 68 | 269.7 | 10.4 | 18 | 14.1606 | 0.67849 | 14.4027 |  |  |  |  | 0.19 | 15.5516 | 0.15212 |  | 0.30876
11:20 | 4040 | 75 | 269.7 | 10.3 | 19 | 14.8716 | 0.67849 | 14.5576 |  |  |  |  | 0.2 | 15.5516 | 0.15552
11:20 | 4040 | 82 | 269.8 | 10.3 | 20 | 15.5516 | 0.67837 | 14.7053 |  |  |  |  | 0.21 | 15.9278 | 0.1574 |  | 0.31731
11:20 | 4041 | 82 | 269.8 | 10.3 | 21 | 15.5516 | 0.67837 | 14.8462 |  |  |  |  | 0.22 | 15.9293 | 0.15929
11:20 | 4042 | 86 | 269.9 | 10.3 | 22 | 15.9278 | 0.67824 | 14.9803 |  |  |  |  | 0.23 | 16.0216 | 0.15975 |  | 0.32012
11:20 | 4043 | 86 | 270 | 10.4 | 23 | 15.9293 | 0.67812 | 15.1078 |  |  |  |  | 0.24 | 16.0216 | 0.16022
11:20 | 4044 | 87 | 270 | 10.4 | 24 | 16.0216 | 0.67812 | 15.2288 |  |  |  |  | 0.25 | 16.294 | 0.16158 |  | 0.32557
11:20 | 4044 | 87 | 270 | 10.4 | 25 | 16.0216 | 0.67812 | 15.3436 |  |  |  |  | 0.26 | 16.4741 | 0.16384
11:20 | 4046 | 90 | 269.9 | 10.4 | 26 | 16.294 | 0.67824 | 15.4521 |  |  |  |  | 0.27 | 16.9158 | 0.16695 |  | 0.33826
11:20 | 4046 | 92 | 269.9 | 10.4 | 27 | 16.4741 | 0.67824 | 15.5547 |  |  |  |  | 0.28 | 17.3399 | 0.17128
11:20 | 4048 | 97 | 269.9 | 10.3 | 28 | 16.9158 | 0.67824 | 15.6514 |  |  |  |  | 0.29 | 17.3399 | 0.1734 |  | 0.34652
11:20 | 4048 | 102 | 269.5 | 10.3 | 29 | 17.3399 | 0.67874 | 15.7424 |  |  |  |  | 0.3 | 17.2563 | 0.17298
11:20 | 4050 | 102 | 269.5 | 10.3 | 30 | 17.3399 | 0.67874 | 15.8278 |  |  |  |  | 0.31 | 17.2563 | 0.17256 |  | 0.34597
11:20 | 4051 | 101 | 269.6 | 10.3 | 31 | 17.2563 | 0.67862 | 15.9077 |  |  |  |  | 0.32 | 17.5107 | 0.17384
11:20 | 4048 | 101 | 269.6 | 10.3 | 32 | 17.2563 | 0.67862 | 15.9824 |  |  |  |  | 0.33 | 17.5123 | 0.17512 |  | 0.35024
11:20 | 4044 | 104 | 269.6 | 10.3 | 33 | 17.5107 | 0.67862 | 16.0519 |  |  |  |  | 0.34 | 17.5123 | 0.17512
11:20 | 4044 | 104 | 269.7 | 10.3 | 34 | 17.5123 | 0.67849 | 16.1164 |  |  |  |  | 0.35 | 17.5139 | 0.17513 |  | 0.35027
11:20 | 4035 | 104 | 269.7 | 10.3 | 35 | 17.5123 | 0.67849 | 16.1759 |  |  |  |  | 0.36 | 17.5139 | 0.17514
11:20 | 4035 | 104 | 269.8 | 10.3 | 36 | 17.5139 | 0.67837 | 16.2307 |  |  |  |  | 0.37 | 17.4375 | 0.17476 |  | 0.34901
11:20 | 4036 | 104 | 269.8 | 10.3 | 37 | 17.5139 | 0.67837 | 16.2809 |  |  |  |  | 0.38 | 17.4375 | 0.17438
11:20 | 4036 | 103 | 270.3 | 10.3 | 38 | 17.4375 | 0.67774 | 16.3266 |  |  |  |  | 0.39 | 16.9236 | 0.17181 |  | 0.3402
11:20 | 4039 | 103 | 270.3 | 10.4 | 39 | 17.4375 | 0.67774 | 16.3679 |  |  |  |  | 0.4 | 16.9267 | 0.16925
11:20 | 4043 | 97 | 270.4 | 10.4 | 40 | 16.9236 | 0.67762 | 16.4049 |  |  |  |  | 0.41 | 17.1003 | 0.17014 |  | 0.34143
11:20 | 4042 | 97 | 270.6 | 10.4 | 41 | 16.9267 | 0.67737 | 16.4379 |  |  |  |  | 0.42 | 17.1003 | 0.171
11:20 | 4042 | 99 | 270.6 | 10.4 | 42 | 17.1003 | 0.67737 | 16.4668 |  |  |  |  | 0.43 | 17.0137 | 0.17057 |  | 0.34057
11:20 | 4041 | 99 | 270.6 | 10.4 | 43 | 17.1003 | 0.67737 | 16.4918 |  |  |  |  | 0.44 | 17.0169 | 0.17015
11:20 | 4035 | 98 | 270.6 | 10.4 | 44 | 17.0137 | 0.67737 | 16.5131 |  |  |  |  | 0.45 | 16.9298 | 0.16973 |  | 0.3383
11:20 | 4035 | 98 | 270.8 | 10.4 | 45 | 17.0169 | 0.67712 | 16.5308 |  |  |  |  | 0.46 | 16.7544 | 0.16842
11:20 | 4036 | 97 | 270.8 | 10.4 | 46 | 16.9298 | 0.67712 | 16.5449 |  |  |  |  | 0.47 | 16.7544 | 0.16754 |  | 0.3336
11:20 | 4036 | 95 | 270.8 | 10.4 | 47 | 16.7544 | 0.67712 | 16.5556 |  |  |  |  | 0.48 | 16.309 | 0.16532
11:20 | 4030 | 95 | 270.8 | 10.4 | 48 | 16.7544 | 0.67712 | 16.563 |  |  |  |  | 0.49 | 16.3105 | 0.1631 |  | 0.3265
11:20 | 4025 | 90 | 270.9 | 10.4 | 49 | 16.309 | 0.67699 | 16.5672 |  |  |  |  | 0.5 | 16.3994 | 0.16355
11:20 | 4019 | 90 | 271 | 10.4 | 50 | 16.3105 | 0.67687 | 16.5684 |  |  |  |  | 0.51 | 16.4877 | 0.16444 |  | 0.32946
11:20 | 4011 | 91 | 270.9 | 10.4 | 51 | 16.3994 | 0.67699 | 16.5665 |  |  |  |  | 0.52 | 16.4877 | 0.16488
11:20 | 4010 | 92 | 270.8 | 10.4 | 52 | 16.4877 | 0.67712 | 16.5618 |  |  |  |  | 0.53 | 16.5756 | 0.16532 |  | 0.33032
11:20 | 4000 | 92 | 270.8 | 10.4 | 53 | 16.4877 | 0.67712 | 16.5544 |  |  |  |  | 0.54 | 16.306 | 0.16441
11:20 | 4000 | 93 | 270.7 | 10.4 | 54 | 16.5756 | 0.67724 | 16.5443 |  |  |  |  | 0.55 | 15.9425 | 0.16124 |  | 0.32006
11:20 | 3985 | 90 | 270.7 | 10.4 | 55 | 16.306 | 0.67724 | 16.5317 |  |  |  |  | 0.56 | 15.9425 | 0.15942
11:20 | 3984 | 86 | 270.9 | 10.4 | 56 | 15.9425 | 0.67699 | 16.5166 |  |  |  |  | 0.57 | 15.3777 | 0.1566 |  | 0.30944
11:20 | 3981 | 86 | 270.9 | 10.4 | 57 | 15.9425 | 0.67699 | 16.4992 |  |  |  |  | 0.58 | 15.3777 | 0.15378
11:20 | 3978 | 80 | 271 | 10.4 | 58 | 15.3777 | 0.67687 | 16.4795 |  |  |  |  | 0.59 | 15.0866 | 0.15232 |  | 0.3027
11:20 | 3976 | 80 | 271 | 10.4 | 59 | 15.3777 | 0.67687 | 16.4576 |  |  |  |  | 0.6 | 15.0866 | 0.15087
11:20 | 3975 | 77 | 271 | 10.4 | 60 | 15.0866 | 0.67687 | 16.4337 |  |  |  |  | 0.61 | 14.8908 | 0.14989 |  | 0.29782
11:20 | 3975 | 77 | 271 | 10.4 | 61 | 15.0866 | 0.67687 | 16.4079 |  |  |  |  | 0.62 | 14.6949 | 0.14793
11:20 | 3978 | 75 | 271.1 | 10.4 | 62 | 14.8908 | 0.67675 | 16.3801 |  |  |  |  | 0.63 | 14.6949 | 0.14695 |  | 0.29388
11:20 | 3978 | 73 | 271.4 | 10.4 | 63 | 14.6949 | 0.67637 | 16.3506 |  |  |  |  | 0.64 | 14.6909 | 0.14693
11:20 | 3994 | 73 | 271.4 | 10.4 | 64 | 14.6949 | 0.67637 | 16.3194 |  |  |  |  | 0.65 | 14.6895 | 0.1469 |  | 0.29313
11:20 | 3995 | 73 | 271.1 | 10.4 | 65 | 14.6909 | 0.67675 | 16.2866 |  |  |  |  | 0.66 | 14.4896 | 0.1459
11:20 | 3997 | 73 | 271 | 10.4 | 66 | 14.6895 | 0.67687 | 16.2522 |  |  |  |  | 0.67 | 14.4909 | 0.1449 |  | 0.29049
11:20 | 3999 | 71 | 271.2 | 10.4 | 67 | 14.4896 | 0.67662 | 16.2164 |  |  |  |  | 0.68 | 14.6936 | 0.14592
11:20 | 3995 | 71 | 271.3 | 10.4 | 68 | 14.4909 | 0.6765 | 16.1792 |  |  |  |  | 0.69 | 14.7925 | 0.14743 |  | 0.29618
11:20 | 3990 | 73 | 271.3 | 10.4 | 69 | 14.6936 | 0.6765 | 16.1408 |  |  |  |  | 0.7 | 14.9911 | 0.14892
11:20 | 3989 | 74 | 271.2 | 10.4 | 70 | 14.7925 | 0.67662 | 16.1011 |  |  |  |  | 0.71 | 15.1829 | 0.15087 |  | 0.30366
11:20 | 3981 | 76 | 271.2 | 10.4 | 71 | 14.9911 | 0.67662 | 16.0604 |  |  |  |  | 0.72 | 15.3763 | 0.1528
11:20 | 3981 | 78 | 270.9 | 10.4 | 72 | 15.1829 | 0.67699 | 16.0185 |  |  |  |  | 0.73 | 15.851 | 0.15614 |  | 0.31544
11:20 | 3973 | 80 | 270.9 | 10.4 | 73 | 15.3763 | 0.67699 | 15.9757 |  |  |  |  | 0.74 | 15.8524 | 0.15852
11:20 | 3972 | 85 | 271 | 10.4 | 74 | 15.851 | 0.67687 | 15.9321 |  |  |  |  | 0.75 | 15.573 | 0.15713 |  | 0.3124
11:20 | 3981 | 85 | 271.1 | 10.4 | 75 | 15.8524 | 0.67675 | 15.8875 |  |  |  |  | 0.76 | 15.5744 | 0.15574
11:20 | 3991 | 82 | 271.3 | 10.4 | 76 | 15.573 | 0.6765 | 15.8422 |  |  |  |  | 0.77 | 15.5744 | 0.15574 |  | 0.31148
11:20 | 3996 | 82 | 271.4 | 10.4 | 77 | 15.5744 | 0.67637 | 15.7963 |  |  |  |  | 0.78 | 15.573 | 0.15574
11:20 | 4003 | 82 | 271.4 | 10.4 | 78 | 15.5744 | 0.67637 | 15.7496 |  |  |  |  | 0.79 | 15.573 | 0.15573 |  | 0.31114
11:20 | 4003 | 82 | 271.3 | 10.4 | 79 | 15.573 | 0.6765 | 15.7025 |  |  |  |  | 0.8 | 15.4778 | 0.15525
11:20 | 4001 | 82 | 271.3 | 10.4 | 80 | 15.573 | 0.6765 | 15.6548 |  |  |  |  | 0.81 | 15.6677 | 0.15573 |  | 0.31334
11:20 | 4001 | 81 | 271.3 | 10.4 | 81 | 15.4778 | 0.6765 | 15.6067 |  |  |  |  | 0.82 | 15.8539 | 0.15761
11:20 | 4003 | 83 | 271.3 | 10.4 | 82 | 15.6677 | 0.6765 | 15.5582 |  |  |  |  | 0.83 | 15.8524 | 0.15853 |  | 0.31579
11:20 | 4004 | 85 | 271.2 | 10.4 | 83 | 15.8539 | 0.67662 | 15.5094 |  |  |  |  | 0.84 | 15.4735 | 0.15663
11:20 | 4000 | 85 | 271.1 | 10.4 | 84 | 15.8524 | 0.67675 | 15.4603 |  |  |  |  | 0.85 | 15.4735 | 0.15474 |  | 0.30752
11:20 | 3996 | 81 | 271 | 10.4 | 85 | 15.4735 | 0.67687 | 15.411 |  |  |  |  | 0.86 | 14.888 | 0.15181
11:20 | 3990 | 81 | 271 | 10.4 | 86 | 15.4735 | 0.67687 | 15.3615 |  |  |  |  | 0.87 | 14.6855 | 0.14787 |  | 0.29405
11:20 | 3979 | 75 | 270.9 | 10.4 | 87 | 14.888 | 0.67699 | 15.312 |  |  |  |  | 0.88 | 14.5845 | 0.14635
11:20 | 3980 | 73 | 270.7 | 10.4 | 88 | 14.6855 | 0.67724 | 15.2624 |  |  |  |  | 0.89 | 14.5886 | 0.14587 |  | 0.29176
11:20 | 3989 | 72 | 270.7 | 10.4 | 89 | 14.5845 | 0.67724 | 15.2128 |  |  |  |  | 0.9 | 14.5886 | 0.14589
11:20 | 3989 | 72 | 271 | 10.4 | 90 | 14.5886 | 0.67687 | 15.1632 |  |  |  |  | 0.91 | 14.6895 | 0.14639 |  | 0.29379
11:20 | 3990 | 72 | 271 | 10.4 | 91 | 14.5886 | 0.67687 | 15.1137 |  |  |  |  | 0.92 | 14.7898 | 0.1474
11:20 | 3990 | 73 | 271 | 10.4 | 92 | 14.6895 | 0.67687 | 15.0644 |  |  |  |  | 0.93 | 15.187 | 0.14988 |  | 0.30242
11:20 | 3990 | 74 | 271 | 10.4 | 93 | 14.7898 | 0.67687 | 15.0152 |  |  |  |  | 0.94 | 15.1884 | 0.15188
11:20 | 3989 | 78 | 271.2 | 10.4 | 94 | 15.187 | 0.67662 | 14.9663 |  |  |  |  | 0.95 | 14.7939 | 0.14991 |  | 0.29686
11:20 | 3987 | 78 | 271.3 | 10.4 | 95 | 15.1884 | 0.6765 | 14.9176 |  |  |  |  | 0.96 | 14.6936 | 0.14744
11:20 | 3984 | 74 | 271.3 | 10.4 | 96 | 14.7939 | 0.6765 | 14.8692 |  |  |  |  | 0.97 | 14.5926 | 0.14643 |  | 0.29218
11:20 | 3984 | 73 | 271.3 | 10.3 | 97 | 14.6936 | 0.6765 | 14.8211 |  |  |  |  | 0.98 | 14.5912 | 0.14592
11:20 | 3983 | 72 | 271.3 | 10.3 | 98 | 14.5926 | 0.6765 | 14.7734 |  |  |  |  | 0.99 | 14.284 | 0.14438 |  | 0.2846
11:20 | 3983 | 72 | 271.2 | 10.3 | 99 | 14.5912 | 0.67662 | 14.7261 |  |  |  |  | 1 | 13.6514 | 0.13968
11:20 | 3991 | 69 | 271.2 | 10.3 | 100 | 14.284 | 0.67662 | 14.6792 |  |  |  |  | 0 | 13.7593 | -13.7053 |  | -13.7246
11:20 | 3993 | 63 | 271.4 | 10.3 | 101 | 13.6514 | 0.67637 | 14.6328 |  |  |  |  | 0.01 | 14.4909 | 0.14125
11:20 | 4001 | 64 | 271.4 | 10.3 | 102 | 13.7593 | 0.67637 | 14.5868 |  |  |  |  | 0.02 | 14.4909 | 0.14491 |  | 0.29116
11:20 | 4007 | 71 | 271.3 | 10.3 | 103 | 14.4909 | 0.6765 | 14.5414 |  |  |  |  | 0.03 | 14.8935 | 0.14692
11:20 | 4012 | 71 | 271.3 | 10.3 | 104 | 14.4909 | 0.6765 | 14.4965 |  |  |  |  | 0.04 | 14.9952 | 0.14944 |  | 0.29989
11:20 | 4020 | 75 | 271.3 | 10.3 | 105 | 14.8935 | 0.6765 | 14.4522 |  |  |  |  | 0.05 | 15.0935 | 0.15044
11:20 | 4020 | 76 | 271.5 | 10.3 | 106 | 14.9952 | 0.67625 | 14.4085 |  |  |  |  | 0.06 | 15.187 | 0.1514 |  | 0.3031
11:20 | 4018 | 77 | 271.5 | 10.3 | 107 | 15.0935 | 0.67625 | 14.3653 |  |  |  |  | 0.07 | 15.0894 | 0.15138
11:20 | 4018 | 78 | 271.2 | 10.3 | 108 | 15.187 | 0.67662 | 14.3228 |  |  |  |  | 0.08 | 14.5899 | 0.1484 |  | 0.29346
11:20 | 4003 | 77 | 271.2 | 10.3 | 109 | 15.0894 | 0.67662 | 14.281 |  |  |  |  | 0.09 | 14.5886 | 0.14589
11:20 | 3999 | 72 | 271.1 | 10.3 | 110 | 14.5899 | 0.67675 | 14.2398 |  |  |  |  | 0.1 | 15.2813 | 0.14935 |  | 0.30331
11:20 | 3990 | 72 | 271 | 10.3 | 111 | 14.5886 | 0.67687 | 14.1992 |  |  |  |  | 0.11 | 15.2799 | 0.15281
11:20 | 3981 | 79 | 271 | 10.3 | 112 | 15.2813 | 0.67687 | 14.1594 |  |  |  |  | 0.12 | 14.8894 | 0.15085 |  | 0.29877
11:20 | 3975 | 79 | 270.9 | 10.3 | 113 | 15.2799 | 0.67699 | 14.1202 |  |  |  |  | 0.13 | 14.7925 | 0.14841
11:20 | 3960 | 75 | 271 | 10.3 | 114 | 14.8894 | 0.67687 | 14.0818 |  |  |  |  | 0.14 | 14.5912 | 0.14692 |  | 0.29214
11:20 | 3959 | 74 | 271.2 | 10.3 | 115 | 14.7925 | 0.67662 | 14.044 |  |  |  |  | 0.15 | 14.4856 | 0.14538
11:20 | 3943 | 72 | 271.2 | 10.3 | 116 | 14.5912 | 0.67662 | 14.007 |  |  |  |  | 0.16 | 14.3832 | 0.14434 |  | 0.28697
11:20 | 3943 | 71 | 270.9 | 10.3 | 117 | 14.4856 | 0.67699 | 13.9707 |  |  |  |  | 0.17 | 14.0716 | 0.14227
11:20 | 3945 | 70 | 270.9 | 10.3 | 118 | 14.3832 | 0.67699 | 13.9352 |  |  |  |  | 0.18 | 13.9675 | 0.1402 |  | 0.27716
11:20 | 3946 | 67 | 270.9 | 10.3 | 119 | 14.0716 | 0.67699 | 13.9003 |  |  |  |  | 0.19 | 13.206 | 0.13587
11:20 | 3950 | 66 | 271 | 10.3 | 120 | 13.9675 | 0.67687 | 13.8662 |  |  |  |  | 0.2 | 13.2072 | 0.13207 |  | 0.26414
11:20 | 3953 | 59 | 271 | 10.3 | 121 | 13.206 | 0.67687 | 13.8328 |  |  |  |  | 0.21 | 13.2072 | 0.13207
11:20 | 3959 | 59 | 271.1 | 10.3 | 122 | 13.2072 | 0.67675 | 13.8002 |  |  |  |  | 0.22 | 13.2097 | 0.13208 |  | 0.26637
11:20 | 3971 | 59 | 271.1 | 10.3 | 123 | 13.2072 | 0.67675 | 13.7682 |  |  |  |  | 0.23 | 13.8651 | 0.13537
11:20 | 3971 | 59 | 271.3 | 10.3 | 124 | 13.2097 | 0.6765 | 13.737 |  |  |  |  | 0.24 | 14.284 | 0.14075 |  | 0.28428
11:20 | 3985 | 65 | 271.3 | 10.3 | 125 | 13.8651 | 0.6765 | 13.7065 |  |  |  |  | 0.25 | 14.284 | 0.14284
11:20 | 3985 | 69 | 271.2 | 10.3 | 126 | 14.284 | 0.67662 | 13.6767 |  |  |  |  | 0.26 | 14.2853 | 0.14285 |  | 0.28571
11:20 | 3984 | 69 | 271.2 | 10.3 | 127 | 14.284 | 0.67662 | 13.6475 |  |  |  |  | 0.27 | 14.2866 | 0.14286
11:20 | 3984 | 69 | 271.3 | 10.3 | 128 | 14.2853 | 0.6765 | 13.6191 |  |  |  |  | 0.28 | 14.8921 | 0.14589 |  | 0.29582
11:20 | 3985 | 69 | 271.4 | 10.3 | 129 | 14.2866 | 0.67637 | 13.5913 |  |  |  |  | 0.29 | 14.8908 | 0.14891
11:20 | 3986 | 75 | 271.2 | 10.3 | 130 | 14.8921 | 0.67662 | 13.5641 |  |  |  |  | 0.3 | 14.9897 | 0.1494 |  | 0.29947
11:20 | 3987 | 75 | 271.1 | 10.3 | 131 | 14.8908 | 0.67675 | 13.5376 |  |  |  |  | 0.31 | 14.9925 | 0.14991
11:20 | 3987 | 76 | 271.1 | 10.3 | 132 | 14.9897 | 0.67675 | 13.5116 |  |  |  |  | 0.32 | 14.7939 | 0.14893 |  | 0.2962
11:20 | 3987 | 76 | 271.3 | 10.3 | 133 | 14.9925 | 0.6765 | 13.4863 |  |  |  |  | 0.33 | 14.6936 | 0.14744
11:20 | 3987 | 74 | 271.3 | 10.3 | 134 | 14.7939 | 0.6765 | 13.4615 |  |  |  |  | 0.34 | 14.7939 | 0.14744 |  | 0.29653
11:20 | 3987 | 73 | 271.3 | 10.3 | 135 | 14.6936 | 0.6765 | 13.4372 |  |  |  |  | 0.35 | 15.0894 | 0.14942
11:20 | 3983 | 74 | 271.3 | 10.3 | 136 | 14.7939 | 0.6765 | 13.4135 |  |  |  |  | 0.36 | 15.0894 | 0.15089 |  | 0.30079
11:20 | 3982 | 77 | 271.2 | 10.3 | 137 | 15.0894 | 0.67662 | 13.3903 |  |  |  |  | 0.37 | 14.7898 | 0.1494
11:20 | 3982 | 77 | 271.2 | 10.3 | 138 | 15.0894 | 0.67662 | 13.3675 |  |  |  |  | 0.38 | 14.7871 | 0.14788 |  | 0.29475
11:20 | 3982 | 74 | 271 | 10.3 | 139 | 14.7898 | 0.67687 | 13.3451 |  |  |  |  | 0.39 | 14.4856 | 0.14636
11:20 | 3981 | 74 | 270.8 | 10.3 | 140 | 14.7871 | 0.67712 | 13.3232 |  |  |  |  | 0.4 | 14.2801 | 0.14383 |  | 0.28559
11:20 | 3977 | 71 | 270.9 | 10.3 | 141 | 14.4856 | 0.67699 | 13.3016 |  |  |  |  | 0.41 | 14.0716 | 0.14176
11:20 | 3977 | 69 | 270.9 | 10.3 | 142 | 14.2801 | 0.67699 | 13.2803 |  |  |  |  | 0.42 | 13.8638 | 0.13968 |  | 0.27797
11:20 | 3976 | 67 | 270.9 | 10.3 | 143 | 14.0716 | 0.67699 | 13.2594 |  |  |  |  | 0.43 | 13.8638 | 0.13864
11:20 | 3976 | 65 | 271.2 | 10.3 | 144 | 13.8638 | 0.67662 | 13.2387 |  |  |  |  | 0.44 | 13.5413 | 0.13703 |  | 0.27191
11:20 | 3973 | 65 | 271.2 | 10.3 | 145 | 13.8638 | 0.67662 | 13.2182 |  |  |  |  | 0.45 | 13.5426 | 0.13542
11:20 | 3972 | 62 | 271.3 | 10.3 | 146 | 13.5413 | 0.6765 | 13.1979 |  |  |  |  | 0.46 | 13.0984 | 0.13321 |  | 0.26345
11:20 | 3971 | 62 | 271.4 | 10.3 | 147 | 13.5426 | 0.67637 | 13.1777 |  |  |  |  | 0.47 | 13.0972 | 0.13098
11:20 | 3970 | 58 | 271.4 | 10.3 | 148 | 13.0984 | 0.67637 | 13.1576 |  |  |  |  | 0.48 | 12.8694 | 0.12983 |  | 0.25815
11:20 | 3972 | 58 | 271.3 | 10.3 | 149 | 13.0972 | 0.6765 | 13.1376 |  |  |  |  | 0.49 | 12.8706 | 0.1287
11:20 | 3978 | 56 | 271.3 | 10.3 | 150 | 12.8694 | 0.6765 | 13.1175 |  |  |  |  | 0.5 | 12.4024 | 0.12637 |  | 0.2484
11:20 | 3979 | 56 | 271.4 | 10.3 | 151 | 12.8706 | 0.67637 | 13.0975 |  |  |  |  | 0.51 | 12.0394 | 0.12221
11:20 | 3998 | 52 | 271.4 | 10.3 | 152 | 12.4024 | 0.67637 | 13.0773 |  |  |  |  | 0.52 | 12.1616 | 0.121 |  | 0.24403
11:20 | 3998 | 49 | 271.4 | 10.3 | 153 | 12.0394 | 0.67637 | 13.0569 |  |  |  |  | 0.53 | 12.5234 | 0.12343
11:20 | 4004 | 50 | 271.4 | 10.3 | 154 | 12.1616 | 0.67637 | 13.0364 |  |  |  |  | 0.54 | 12.5246 | 0.12524 |  | 0.25049
11:20 | 4007 | 53 | 271.6 | 10.3 | 155 | 12.5234 | 0.67612 | 13.0155 |  |  |  |  | 0.55 | 12.5246 | 0.12525
11:20 | 4001 | 53 | 271.7 | 10.3 | 156 | 12.5246 | 0.676 | 12.9944 |  |  |  |  | 0.56 | 12.5246 | 0.12525 |  | 0.24764
11:20 | 3995 | 53 | 271.7 | 10.3 | 157 | 12.5246 | 0.676 | 12.9729 |  |  |  |  | 0.57 | 11.6682 | 0.12096
11:20 | 3993 | 53 | 271.7 | 10.3 | 158 | 12.5246 | 0.676 | 12.951 |  |  |  |  | 0.58 | 11.1514 | 0.1141 |  | 0.22431
11:20 | 3985 | 46 | 271.7 | 10.3 | 159 | 11.6682 | 0.676 | 12.9285 |  |  |  |  | 0.59 | 11.0179 | 0.11085
11:20 | 3986 | 42 | 271.9 | 10.3 | 160 | 11.1514 | 0.67575 | 12.9055 |  |  |  |  | 0.6 | 11.0209 | 0.11019 |  | 0.22085
11:20 | 4003 | 41 | 271.9 | 10.3 | 161 | 11.0179 | 0.67575 | 12.8819 |  |  |  |  | 0.61 | 11.1545 | 0.11088
11:20 | 4003 | 41 | 272.2 | 10.3 | 162 | 11.0209 | 0.67538 | 12.8575 |  |  |  |  | 0.62 | 11.7976 | 0.11476 |  | 0.2338
11:20 | 4008 | 42 | 272.2 | 10.3 | 163 | 11.1545 | 0.67538 | 12.8325 |  |  |  |  | 0.63 | 11.7965 | 0.11797
11:20 | 4011 | 47 | 272 | 10.3 | 164 | 11.7976 | 0.67563 | 12.8066 |  |  |  |  | 0.64 | 12.4081 | 0.12102 |  | 0.24612
11:20 | 4011 | 47 | 271.9 | 10.3 | 165 | 11.7965 | 0.67575 | 12.7797 |  |  |  |  | 0.65 | 12.407 | 0.12408
11:21 | 4011 | 52 | 271.9 | 10.3 | 166 | 12.4081 | 0.67575 | 12.752 |  |  |  |  | 0.66 | 13.2157 | 0.12811 |  | 0.2638
11:21 | 4012 | 52 | 271.8 | 10.3 | 167 | 12.407 | 0.67588 | 12.7231 |  |  |  |  | 0.67 | 13.8714 | 0.13544
11:21 | 4019 | 59 | 271.8 | 10.3 | 168 | 13.2157 | 0.67588 | 12.6932 |  |  |  |  | 0.68 | 13.3273 | 0.13599 |  | 0.26724
11:21 | 4019 | 65 | 271.8 | 10.3 | 169 | 13.8714 | 0.67588 | 12.662 |  |  |  |  | 0.69 | 12.9922 | 0.1316
11:21 | 4014 | 60 | 271.8 | 10.3 | 170 | 13.3273 | 0.67588 | 12.6296 |  |  |  |  | 0.7 | 12.8777 | 0.12935 |  | 0.25434
11:21 | 4014 | 57 | 272 | 10.3 | 171 | 12.9922 | 0.67563 | 12.5958 |  |  |  |  | 0.71 | 11.7987 | 0.12338
11:21 | 4016 | 56 | 272 | 10.3 | 172 | 12.8777 | 0.67563 | 12.5606 |  |  |  |  | 0.72 | 11.7998 | 0.11799 |  | 0.23642
11:21 | 4018 | 47 | 272.1 | 10.3 | 173 | 11.7987 | 0.6755 | 12.5239 |  |  |  |  | 0.73 | 11.9268 | 0.11863
11:21 | 4023 | 47 | 272.2 | 10.3 | 174 | 11.7998 | 0.67538 | 12.4855 |  |  |  |  | 0.74 | 11.9279 | 0.11927 |  | 0.24018
11:21 | 4028 | 48 | 272.4 | 10.3 | 175 | 11.9268 | 0.67513 | 12.4455 |  |  |  |  | 0.75 | 12.415 | 0.12171
11:21 | 4027 | 48 | 272.5 | 10.3 | 176 | 11.9279 | 0.67501 | 12.4036 |  |  |  |  | 0.76 | 12.7681 | 0.12592 |  | 0.2522
11:21 | 4025 | 52 | 272.5 | 10.3 | 177 | 12.415 | 0.67501 | 12.36 |  |  |  |  | 0.77 | 12.1739 | 0.12471
11:21 | 4025 | 55 | 272.5 | 10.3 | 178 | 12.7681 | 0.67501 | 12.3143 |  |  |  |  | 0.78 | 11.6714 | 0.11923 |  | 0.2351
11:21 | 4012 | 50 | 272.5 | 10.3 | 179 | 12.1739 | 0.67501 | 12.2666 |  |  |  |  | 0.79 | 11.6714 | 0.11671
11:21 | 4012 | 46 | 272 | 10.3 | 180 | 11.6714 | 0.67563 | 12.2167 |  |  |  |  | 0.8 | 11.2854 | 0.11478 |  | 0.227
11:21 | 4010 | 46 | 272 | 10.3 | 181 | 11.6714 | 0.67563 | 12.1646 |  |  |  |  | 0.81 | 11.2854 | 0.11285
11:21 | 4009 | 43 | 272.1 | 10.3 | 182 | 11.2854 | 0.6755 | 12.1101 |  |  |  |  | 0.82 | 11.0219 | 0.11154 |  | 0.22132
11:21 | 4009 | 43 | 272.1 | 10.3 | 183 | 11.2854 | 0.6755 | 12.0532 |  |  |  |  | 0.83 | 11.0229 | 0.11022
11:21 | 4008 | 41 | 272.3 | 10.3 | 184 | 11.0219 | 0.67526 | 11.9938 |  |  |  |  | 0.84 | 11.2886 | 0.11156 |  | 0.22531
11:21 | 4010 | 41 | 272.4 | 10.3 | 185 | 11.0229 | 0.67513 | 11.9317 |  |  |  |  | 0.85 | 11.417 | 0.11353
11:21 | 4035 | 43 | 272.4 | 10.3 | 186 | 11.2886 | 0.67513 | 11.8669 |  |  |  |  | 0.86 | 11.546 | 0.11481 |  | 0.23092
11:21 | 4035 | 44 | 272.2 | 10.3 | 187 | 11.417 | 0.67538 | 11.7992 |  |  |  |  | 0.87 | 11.6757 | 0.11611
11:21 | 4039 | 45 | 272.2 | 10.3 | 188 | 11.546 | 0.67538 | 11.7285 |  |  |  |  | 0.88 | 11.6757 | 0.11676 |  | 0.2335
11:21 | 4039 | 46 | 272.4 | 10.3 | 189 | 11.6757 | 0.67513 | 11.6548 |  |  |  |  | 0.89 | 11.6725 | 0.11674
11:21 | 4035 | 46 | 272.4 | 10.3 | 190 | 11.6757 | 0.67513 | 11.5779 |  |  |  |  | 0.9 | 11.6704 | 0.11671 |  | 0.23342
11:21 | 4032 | 46 | 272.1 | 10.3 | 191 | 11.6725 | 0.6755 | 11.4976 |  |  |  |  | 0.91 | 11.6725 | 0.11671
11:21 | 4024 | 46 | 271.9 | 10.3 | 192 | 11.6704 | 0.67575 | 11.414 |  |  |  |  | 0.92 | 11.6736 | 0.11673 |  | 0.23347
11:21 | 4015 | 46 | 272.1 | 10.3 | 193 | 11.6725 | 0.6755 | 11.3269 |  |  |  |  | 0.93 | 11.6736 | 0.11674
11:21 | 4014 | 46 | 272.2 | 10.3 | 194 | 11.6736 | 0.67538 | 11.2361 |  |  |  |  | 0.94 | 11.6704 | 0.11672 |  | 0.23342
11:21 | 3998 | 46 | 272.2 | 10.3 | 195 | 11.6736 | 0.67538 | 11.1416 |  |  |  |  | 0.95 | 11.6704 | 0.1167
11:21 | 3998 | 46 | 271.9 | 10.4 | 196 | 11.6704 | 0.67575 | 11.0432 |  |  |  |  | 0.96 | 11.6704 | 0.1167 |  | 0.23341
11:21 | 3995 | 46 | 271.9 | 10.4 | 197 | 11.6704 | 0.67575 | 10.9408 |  |  |  |  | 0.97 | 11.6704 | 0.1167
11:21 | 3995 | 46 | 271.9 | 10.4 | 198 | 11.6704 | 0.67575 | 10.8343 |  |  |  |  | 0.98 | 11.7976 | 0.11734 |  | 0.23553
11:21 | 3997 | 46 | 271.9 | 10.4 | 199 | 11.6704 | 0.67575 | 10.7235 |  |  |  |  | 0.99 | 11.7987 | 0.11798
11:21 | 3999 | 47 | 272 | 10.4 | 200 | 11.7976 | 0.67563 | 10.6084 |  |  |  |  | 1 | 11.418 | 0.11608
11:21 | 3999 | 47 | 272.1 | 10.4 | 201 | 11.7987 | 0.6755 | 10.4888
11:21 | 4000 | 44 | 272.3 | 10.4 | 202 | 11.418 | 0.67526 | 10.3645
11:21 | 4001 | 44 | 272.4 | 10.4 | 203 | 11.4191 | 0.67513 | 10.2355
11:21 | 4016 | 40 | 272.4 | 10.4 | 204 | 10.8876 | 0.67513 | 10.1016
11:21 | 4016 | 36 | 272.2 | 10.4 | 205 | 10.327 | 0.67538 | 9.9627
11:21 | 4028 | 33 | 272.2 | 10.4 | 206 | 9.8874 | 0.67538 | 9.8186
11:21 | 4029 | 29 | 272.4 | 10.4 | 207 | 9.2705 | 0.67513 | 9.6692
11:21 | 4034 | 29 | 272.5 | 10.4 | 208 | 9.2713 | 0.67501 | 9.5144
11:21 | 4039 | 27 | 272.4 | 10.4 | 209 | 8.9451 | 0.67513 | 9.354
11:21 | 4048 | 27 | 272.4 | 10.4 | 210 | 8.9451 | 0.67513 | 9.1879
11:21 | 4057 | 32 | 272.2 | 10.4 |  | 9.7364 | 0.67538
11:21 | 4057 | 32 | 272.1 | 10.4 |  | 9.7355 | 0.6755
11:21 | 4048 | 35 | 272.1 | 10.4 |  | 10.1817 | 0.6755
11:21 | 4048 | 37 | 272.1 | 10.4 |  | 10.4685 | 0.6755
11:21 | 4029 | 35 | 272.1 | 10.4 |  | 10.1817 | 0.6755
11:21 | 4028 | 32 | 272 | 10.4 |  | 9.7346 | 0.67563
11:21 | 4020 | 32 | 272 | 10.4 |  | 9.7346 | 0.67563
11:21 | 4014 | 34 | 272 | 10.4 |  | 10.0342 | 0.67563
11:21 | 4008 | 34 | 271.9 | 10.4 |  | 10.0333 | 0.67575
11:21 | 4000 | 24 | 272 | 10.4 |  | 8.4304 | 0.67563
11:21 | 4000 | 23 | 272.1 | 10.4 |  | 8.2537 | 0.6755
11:21 | 4009 | 20 | 272.1 | 10.4 |  | 7.6966 | 0.6755
11:21 | 4009 | 18 | 272.7 | 10.4 |  | 7.3057 | 0.67476
11:21 | 4022 | 22 | 272.7 | 10.4 |  | 8.0767 | 0.67476
11:21 | 4024 | 28 | 272.7 | 10.4 |  | 9.1118 | 0.67476
11:21 | 4029 | 28 | 272.7 | 10.4 |  | 9.1118 | 0.67476
11:21 | 4034 | 29 | 272.8 | 10.4 |  | 9.2739 | 0.67464
11:21 | 4036 | 29 | 272.9 | 10.4 |  | 9.2747 | 0.67452
11:21 | 4037 | 25 | 272.7 | 10.4 |  | 8.6098 | 0.67476
11:21 | 4037 | 25 | 272.5 | 10.4 |  | 8.6082 | 0.67501
11:21 | 4032 | 23 | 272.5 | 10.4 |  | 8.2567 | 0.67501
11:21 | 4032 | 20 | 272.6 | 10.4 |  | 7.7001 | 0.67489
11:21 | 4035 | 18 | 272.6 | 10.4 |  | 7.305 | 0.67489
11:21 | 4035 | 14 | 272.8 | 10.4 |  | 6.4436 | 0.67464
11:21 | 4039 | 14 | 272.9 | 10.4 |  | 6.4442 | 0.67452
11:21 | 4042 | 13 | 272.9 | 10.4 |  | 6.2098 | 0.67452
11:21 | 4041 | 13 | 272.9 | 10.4 |  | 6.2098 | 0.67452
11:21 | 4039 | 13 | 272.8 | 10.4 |  | 6.2092 | 0.67464
11:21 | 4039 | 13 | 272.7 | 10.4 |  | 6.2086 | 0.67476
11:21 | 4040 | 15 | 272.7 | 10.4 |  | 6.6691 | 0.67476
11:21 | 4040 | 17 | 272.7 | 10.4 |  | 7.0998 | 0.67476
11:21 | 4043 | 16 | 272.7 | 10.3 |  | 6.8878 | 0.67476
11:21 | 4043 | 14 | 272.8 | 10.3 |  | 6.4436 | 0.67464
11:21 | 4035 | 14 | 272.8 | 10.3 |  | 6.4436 | 0.67464
11:21 | 4027 | 15 | 272.7 | 10.3 |  | 6.6691 | 0.67476
11:21 | 4030 | 15 | 272.7 | 10.3 |  | 6.6691 | 0.67476
11:21 | 4034 | 16 | 272.7 | 10.3 |  | 6.8878 | 0.67476
11:21 | 4034 | 16 | 272.7 | 10.3 |  | 6.8878 | 0.67476
11:21 | 4046 | 22 | 272.7 | 10.3 |  | 8.0767 | 0.67476
11:21 | 4046 | 27 | 272.7 | 10.4 |  | 8.9476 | 0.67476
11:21 | 4056 | 29 | 272.7 | 10.4 |  | 9.273 | 0.67476
11:21 | 4057 | 32 | 272.7 | 10.4 |  | 9.7409 | 0.67476
11:21 | 4057 | 32 | 272.7 | 10.4 |  | 9.7409 | 0.67476
11:21 | 4057 | 28 | 272.6 | 10.4 |  | 9.1109 | 0.67489
11:21 | 4056 | 28 | 272.6 | 10.4 |  | 9.1109 | 0.67489
11:21 | 4054 | 23 | 272.6 | 10.4 |  | 8.2575 | 0.67489
11:21 | 4054 | 23 | 272.5 | 10.4 |  | 8.2567 | 0.67501
11:21 | 4049 | 21 | 272.5 | 10.4 |  | 7.8896 | 0.67501
11:21 | 4049 | 20 | 272.7 | 10.4 |  | 7.7008 | 0.67476
11:21 | 4047 | 22 | 272.7 | 10.4 |  | 8.0767 | 0.67476
11:21 | 4046 | 26 | 272.7 | 10.4 |  | 8.7803 | 0.67476
11:21 | 4036 | 26 | 272.7 | 10.4 |  | 8.7803 | 0.67476
11:21 | 4028 | 32 | 272.7 | 10.4 |  | 9.7409 | 0.67476
11:21 | 4019 | 32 | 272.7 | 10.4 |  | 9.7409 | 0.67476
11:21 | 4006 | 29 | 272.6 | 10.4 |  | 9.2722 | 0.67489
11:21 | 4005 | 29 | 272.4 | 10.4 |  | 9.2705 | 0.67513
11:21 | 3986 | 34 | 272.4 | 10.4 |  | 10.0379 | 0.67513
11:21 | 3986 | 39 | 272.3 | 10.4 |  | 10.7497 | 0.67526
11:21 | 3970 | 40 | 272.3 | 10.4 |  | 10.8866 | 0.67526
11:21 | 3967 | 42 | 272 | 10.4 |  | 11.1524 | 0.67563
11:21 | 3973 | 42 | 271.9 | 10.4 |  | 11.1514 | 0.67575
11:21 | 3978 | 43 | 271.8 | 10.4 |  | 11.2823 | 0.67588
11:21 | 3979 | 43 | 271.8 | 10.4 |  | 11.2823 | 0.67588
11:21 | 3980 | 54 | 271.8 | 10.4 |  | 12.6433 | 0.67588
11:21 | 3979 | 57 | 272 | 10.4 |  | 12.9922 | 0.67563
11:21 | 3961 | 56 | 272 | 10.4 |  | 12.8777 | 0.67563
11:21 | 3961 | 56 | 272 | 10.4 |  | 12.8777 | 0.67563
11:21 | 3969 | 53 | 272 | 10.4 |  | 12.528 | 0.67563
11:21 | 3972 | 47 | 271.8 | 10.4 |  | 11.7954 | 0.67588
11:21 | 3977 | 47 | 271.7 | 10.4 |  | 11.7944 | 0.676
11:21 | 3983 | 46 | 271.8 | 10.4 |  | 11.6693 | 0.67588
11:21 | 3988 | 46 | 272 | 10.3 |  | 11.6714 | 0.67563
11:21 | 3999 | 45 | 271.9 | 10.3 |  | 11.5428 | 0.67575
11:21 | 3999 | 44 | 271.8 | 10.3 |  | 11.4128 | 0.67588
11:21 | 4008 | 46 | 271.8 | 10.3 |  | 11.6693 | 0.67588
11:21 | 4008 | 47 | 271.7 | 10.3 |  | 11.7944 | 0.676
11:21 | 4007 | 49 | 271.7 | 10.4 |  | 12.0427 | 0.676
11:21 | 4006 | 53 | 271.8 | 10.4 |  | 12.5257 | 0.67588
11:21 | 4004 | 54 | 271.9 | 10.4 |  | 12.6445 | 0.67575
11:21 | 4002 | 60 | 271.9 | 10.4 |  | 13.3285 | 0.67575
11:21 | 4003 | 60 | 271.9 | 10.4 |  | 13.3285 | 0.67575
11:21 | 4006 | 58 | 271.8 | 10.4 |  | 13.1033 | 0.67588
11:21 | 4006 | 57 | 271.6 | 10.4 |  | 12.9874 | 0.67612
11:21 | 4001 | 55 | 271.6 | 10.4 |  | 12.7575 | 0.67612
11:21 | 4001 | 54 | 271.5 | 10.4 |  | 12.6399 | 0.67625
11:21 | 4009 | 54 | 271.5 | 10.4 |  | 12.6399 | 0.67625
11:21 | 4012 | 54 | 271.8 | 10.4 |  | 12.6433 | 0.67588
11:21 | 4020 | 54 | 271.9 | 10.4 |  | 12.6445 | 0.67575
11:21 | 4027 | 51 | 271.8 | 10.4 |  | 12.2871 | 0.67588
11:21 | 4027 | 51 | 271.7 | 10.3 |  | 12.286 | 0.676
11:21 | 4026 | 53 | 271.6 | 10.3 |  | 12.5234 | 0.67612
11:21 | 4026 | 54 | 271.5 | 10.3 |  | 12.6399 | 0.67625
11:21 | 4028 | 56 | 271.5 | 10.3 |  | 12.8718 | 0.67625
11:21 | 4028 | 58 | 271.7 | 10.3 |  | 13.1021 | 0.676
11:21 | 4026 | 59 | 271.7 | 10.3 |  | 13.2145 | 0.676
11:21 | 4026 | 63 | 271.9 | 10.3 |  | 13.6576 | 0.67575
11:21 | 4030 | 63 | 271.9 | 10.3 |  | 13.6576 | 0.67575
11:21 | 4035 | 55 | 272 | 10.3 |  | 12.7622 | 0.67563
11:21 | 4034 | 55 | 272 | 10.3 |  | 12.7622 | 0.67563
11:21 | 4033 | 59 | 272 | 10.3 |  | 13.2182 | 0.67563
11:21 | 4033 | 60 | 272 | 10.3 |  | 13.3297 | 0.67563
11:21 | 4037 | 59 | 272 | 10.4 |  | 13.2182 | 0.67563
11:21 | 4037 | 59 | 272 | 10.4 |  | 13.2182 | 0.67563
11:21 | 4037 | 59 | 272 | 10.4 |  | 13.2182 | 0.67563
11:21 | 4037 | 62 | 271.9 | 10.4 |  | 13.5488 | 0.67575
11:21 | 4036 | 62 | 271.9 | 10.3 |  | 13.5488 | 0.67575
11:21 | 4034 | 65 | 272.1 | 10.3 |  | 13.8753 | 0.6755
11:21 | 4034 | 65 | 272.3 | 10.3 |  | 13.8778 | 0.67526
11:21 | 4032 | 64 | 272.3 | 10.3 |  | 13.7706 | 0.67526
11:21 | 4032 | 63 | 272.4 | 10.3 |  | 13.6639 | 0.67513
11:21 | 4037 | 59 | 272.4 | 10.3 |  | 13.223 | 0.67513
11:21 | 4037 | 57 | 272.4 | 10.3 |  | 12.997 | 0.67513
11:21 | 4038 | 58 | 272.4 | 10.3 |  | 13.1105 | 0.67513
11:21 | 4039 | 63 | 272.4 | 10.3 |  | 13.6639 | 0.67513
11:21 | 4039 | 63 | 272.4 | 10.3 |  | 13.6639 | 0.67513
11:21 | 4039 | 64 | 272.1 | 10.3 |  | 13.7681 | 0.6755
11:21 | 4041 | 64 | 272 | 10.4 |  | 13.7669 | 0.67563
11:21 | 4050 | 70 | 272 | 10.4 |  | 14.3977 | 0.67563
11:21 | 4050 | 74 | 271.9 | 10.3 |  | 14.802 | 0.67575
11:21 | 4053 | 74 | 271.9 | 10.3 |  | 14.802 | 0.67575
11:21 | 4053 | 74 | 271.9 | 10.3 |  | 14.802 | 0.67575
11:21 | 4054 | 73 | 271.9 | 10.3 |  | 14.7017 | 0.67575
11:21 | 4055 | 63 | 271.9 | 10.3 |  | 13.6576 | 0.67575
11:21 | 4056 | 63 | 271.9 | 10.3 |  | 13.6576 | 0.67575
11:21 | 4057 | 61 | 272 | 10.3 |  | 13.4403 | 0.67563
11:21 | 4058 | 61 | 272.1 | 10.3 |  | 13.4416 | 0.6755
11:21 | 4060 | 62 | 272.1 | 10.3 |  | 13.5513 | 0.6755
11:21 | 4060 | 63 | 272.3 | 10.3 |  | 13.6626 | 0.67526
11:21 | 4062 | 66 | 272.3 | 10.3 |  | 13.9842 | 0.67526
11:21 | 4062 | 68 | 272.3 | 10.3 |  | 14.1945 | 0.67526
11:21 | 4063 | 69 | 272.3 | 10.3 |  | 14.2984 | 0.67526
11:21 | 4064 | 71 | 272.2 | 10.3 |  | 14.5029 | 0.67538
11:21 | 4061 | 71 | 272.1 | 10.3 |  | 14.5015 | 0.6755
11:21 | 4058 | 72 | 272.2 | 10.3 |  | 14.6046 | 0.67538
11:21 | 4056 | 72 | 272.2 | 10.4 |  | 14.6046 | 0.67538
11:21 | 4042 | 74 | 272.2 | 10.4 |  | 14.8061 | 0.67538
11:21 | 4042 | 76 | 272.3 | 10.4 |  | 15.0062 | 0.67526
11:21 | 4035 | 76 | 272.3 | 10.4 |  | 15.0062 | 0.67526
11:21 | 4035 | 76 | 272.4 | 10.4 |  | 15.0076 | 0.67513
11:21 | 4030 | 76 | 272.4 | 10.4 |  | 15.0076 | 0.67513
11:21 | 4027 | 72 | 272.3 | 10.4 |  | 14.606 | 0.67526
11:21 | 4027 | 71 | 272.2 | 10.4 |  | 14.5029 | 0.67538
11:21 | 4027 | 65 | 272.4 | 10.4 |  | 13.8791 | 0.67513
11:21 | 4026 | 65 | 272.5 | 10.3 |  | 13.8804 | 0.67501
11:21 | 4020 | 63 | 272.5 | 10.3 |  | 13.6651 | 0.67501
11:21 | 4020 | 62 | 272.6 | 10.3 |  | 13.5575 | 0.67489
11:21 | 4026 | 59 | 272.6 | 10.3 |  | 13.2254 | 0.67489
11:21 | 4026 | 56 | 272.8 | 10.3 |  | 12.8872 | 0.67464
11:21 | 4021 | 57 | 272.8 | 10.3 |  | 13.0017 | 0.67464
11:21 | 4016 | 60 | 272.6 | 10.3 |  | 13.337 | 0.67489
11:21 | 4019 | 60 | 272.4 | 10.3 |  | 13.3346 | 0.67513
11:21 | 4021 | 63 | 272.4 | 10.3 |  | 13.6639 | 0.67513
11:21 | 4021 | 63 | 272.4 | 10.3 |  | 13.6639 | 0.67513
11:21 | 4021 | 65 | 272.4 | 10.3 |  | 13.8791 | 0.67513
11:21 | 4021 | 67 | 272.3 | 10.3 |  | 14.0897 | 0.67526
11:21 | 4004 | 74 | 272.3 | 10.3 |  | 14.8074 | 0.67526
11:21 | 4004 | 80 | 272.4 | 10.3 |  | 15.3975 | 0.67513
11:21 | 4007 | 80 | 272.4 | 10.3 |  | 15.3975 | 0.67513
11:21 | 4009 | 77 | 272.5 | 10.3 |  | 15.1074 | 0.67501
11:21 | 4011 | 77 | 272.6 | 10.3 |  | 15.1088 | 0.67489
11:21 | 4013 | 80 | 272.5 | 10.3 |  | 15.3989 | 0.67501
11:21 | 4012 | 80 | 272.3 | 10.3 |  | 15.396 | 0.67526
11:21 | 4004 | 79 | 272.3 | 10.3 |  | 15.2995 | 0.67526
11:21 | 4004 | 78 | 271.9 | 10.4 |  | 15.1968 | 0.67575
11:21 | 4003 | 78 | 271.9 | 10.4 |  | 15.1968 | 0.67575
11:21 | 4003 | 77 | 271.8 | 10.4 |  | 15.0977 | 0.67588
11:21 | 3997 | 77 | 271.8 | 10.4 |  | 15.0977 | 0.67588
11:21 | 3992 | 91 | 271.9 | 10.4 |  | 16.4144 | 0.67575
11:21 | 3994 | 91 | 272 | 10.4 |  | 16.4159 | 0.67563
11:21 | 3997 | 93 | 272.1 | 10.4 |  | 16.5969 | 0.6755
11:21 | 3998 | 93 | 272.1 | 10.4 |  | 16.5969 | 0.6755
11:21 | 4015 | 91 | 272.1 | 10.4 |  | 16.4174 | 0.6755
11:21 | 4015 | 89 | 272.1 | 10.4 |  | 16.236 | 0.6755
11:21 | 4014 | 86 | 272.1 | 10.4 |  | 15.96 | 0.6755
11:21 | 4014 | 81 | 272.4 | 10.4 |  | 15.4934 | 0.67513
11:21 | 4014 | 82 | 272.4 | 10.4 |  | 15.5887 | 0.67513
11:21 | 4014 | 87 | 272.4 | 10.4 |  | 16.057 | 0.67513
11:21 | 4016 | 87 | 272.4 | 10.3 |  | 16.057 | 0.67513
11:21 | 4018 | 93 | 272.2 | 10.3 |  | 16.5984 | 0.67538
11:21 | 4018 | 93 | 271.9 | 10.3 |  | 16.5938 | 0.67575
11:21 | 4015 | 102 | 271.9 | 10.3 |  | 17.3782 | 0.67575
11:21 | 4015 | 109 | 271.6 | 10.3 |  | 17.9597 | 0.67612
11:21 | 4034 | 102 | 271.6 | 10.3 |  | 17.3734 | 0.67612
11:21 | 4036 | 93 | 271.2 | 10.3 |  | 16.5832 | 0.67662
11:21 | 4044 | 93 | 271.1 | 10.3 |  | 16.5816 | 0.67675
11:21 | 4050 | 94 | 271.1 | 10.3 |  | 16.6706 | 0.67675
11:21 | 4050 | 94 | 271.1 | 10.3 |  | 16.6706 | 0.67675
11:21 | 4049 | 99 | 271 | 10.3 |  | 17.1066 | 0.67687
11:21 | 4049 | 100 | 271 | 10.3 |  | 17.1928 | 0.67687
11:21 | 4052 | 97 | 271 | 10.3 |  | 16.9329 | 0.67687
11:21 | 4052 | 94 | 271.2 | 10.3 |  | 16.6721 | 0.67662
11:21 | 4049 | 93 | 271.2 | 10.3 |  | 16.5832 | 0.67662
11:21 | 4049 | 91 | 271.1 | 10.3 |  | 16.4024 | 0.67675
11:21 | 4044 | 91 | 271.1 | 10.3 |  | 16.4024 | 0.67675
11:21 | 4040 | 92 | 270.9 | 10.3 |  | 16.4892 | 0.67699
11:21 | 4040 | 92 | 270.8 | 10.3 |  | 16.4877 | 0.67712
11:21 | 4039 | 101 | 270.8 | 10.3 |  | 17.2754 | 0.67712
11:21 | 4039 | 101 | 270.9 | 10.3 |  | 17.2769 | 0.67699
11:21 | 4030 | 100 | 270.9 | 10.3 |  | 17.1912 | 0.67699
11:21 | 4030 | 98 | 270.9 | 10.3 |  | 17.0184 | 0.67699
11:21 | 4025 | 97 | 270.9 | 10.3 |  | 16.9314 | 0.67699
11:21 | 4025 | 95 | 271.2 | 10.3 |  | 16.7605 | 0.67662
11:21 | 4030 | 95 | 271.3 | 10.3 |  | 16.7621 | 0.6765
11:21 | 4035 | 88 | 271.4 | 10.3 |  | 16.1342 | 0.67637
11:21 | 4036 | 88 | 271.5 | 10.3 |  | 16.1357 | 0.67625
11:21 | 4037 | 84 | 271.5 | 10.3 |  | 15.7647 | 0.67625
11:21 | 4037 | 83 | 271.4 | 10.3 |  | 15.6691 | 0.67637
11:21 | 4047 | 81 | 271.4 | 10.3 |  | 15.4792 | 0.67637
11:21 | 4047 | 79 | 271.4 | 10.3 |  | 15.2869 | 0.67637
11:21 | 4043 | 82 | 271.4 | 10.3 |  | 15.5744 | 0.67637
11:21 | 4043 | 86 | 271.1 | 10.3 |  | 15.9454 | 0.67675
11:21 | 4040 | 86 | 271.1 | 10.3 |  | 15.9454 | 0.67675
11:21 | 4037 | 87 | 271.3 | 10.3 |  | 16.0408 | 0.6765
11:21 | 4038 | 87 | 271.4 | 10.3 |  | 16.0423 | 0.67637
11:21 | 4040 | 77 | 271.5 | 10.3 |  | 15.0935 | 0.67625
11:21 | 4039 | 75 | 271.5 | 10.3 |  | 14.8962 | 0.67625
11:21 | 4028 | 75 | 271.5 | 10.3 |  | 14.8962 | 0.67625
11:21 | 4028 | 74 | 271.4 | 10.3 |  | 14.7952 | 0.67637
11:21 | 4023 | 71 | 271.4 | 10.3 |  | 14.4922 | 0.67637
11:21 | 4022 | 65 | 271.1 | 10.3 |  | 13.8625 | 0.67675
11:21 | 4030 | 65 | 271 | 10.3 |  | 13.8613 | 0.67687
11:21 | 4038 | 62 | 271.2 | 10.3 |  | 13.5401 | 0.67662
11:21 | 4037 | 62 | 271.3 | 10.4 |  | 13.5413 | 0.6765
11:21 | 4035 | 55 | 271.1 | 10.4 |  | 12.7517 | 0.67675
11:21 | 4035 | 54 | 270.6 | 10.4 |  | 12.6294 | 0.67737

## Sheet1
| Port | 7
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current
| Pa | Pa | Deg C | mA
Averages | 3975.7898 | 46.3857 | 261.5374 | 10.345 | [11 empty] | 12.7131 |  | 12.5748
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current |  |  |  |  | a | b | n | h | xi | f(xi) | Aj
| Pa. | Pa | Deg C | mA |  | 11.5295 |  |  | 0 | 1 | 100 | 0.01 | 0 | 7.9981
[6 empty] | vel | dens | [5 empty] | 0.01 | 8.2066 | 0.081024 |  | 0.16412
11:35 | 3985 | 19 | 259 | 10.3 | 1 | 7.4111 | 0.69213 | 7.9981 |  |  |  |  | 0.02 | 8.4116 | 0.083091
11:35 | 4000 | 20 | 259 | 10.3 | 2 | 7.6036 | 0.69213 | 8.2066 |  |  |  |  | 0.03 | 8.6131 | 0.085124 |  | 0.17225
11:35 | 4009 | 24 | 259.1 | 10.3 | 3 | 8.3301 | 0.692 | 8.4116 |  |  |  |  | 0.04 | 8.8111 | 0.087121
11:35 | 4009 | 24 | 259.1 | 10.3 | 4 | 8.3301 | 0.692 | 8.6131 |  |  |  |  | 0.05 | 9.0057 | 0.089084 |  | 0.1801
11:35 | 4010 | 23 | 259.2 | 10.3 | 5 | 8.1555 | 0.69187 | 8.8111 |  |  |  |  | 0.06 | 9.1968 | 0.091013
11:35 | 4009 | 22 | 259.2 | 10.3 | 6 | 7.9762 | 0.69187 | 9.0057 |  |  |  |  | 0.07 | 9.3846 | 0.092907 |  | 0.18768
11:35 | 3998 | 24 | 259.2 | 10.3 | 7 | 8.3309 | 0.69187 | 9.1968 |  |  |  |  | 0.08 | 9.5689 | 0.094768
11:35 | 3998 | 25 | 259 | 10.3 | 8 | 8.5011 | 0.69213 | 9.3846 |  |  |  |  | 0.09 | 9.75 | 0.096595 |  | 0.19499
11:35 | 3998 | 24 | 259 | 10.3 | 9 | 8.3293 | 0.69213 | 9.5689 |  |  |  |  | 0.1 | 9.9277 | 0.098388
11:35 | 3998 | 24 | 259 | 10.3 | 10 | 8.3293 | 0.69213 | 9.75 |  |  |  |  | 0.11 | 10.1021 | 0.10015 |  | 0.20203
11:35 | 4001 | 24 | 258.9 | 10.3 | 11 | 8.3286 | 0.69226 | 9.9277 |  |  |  |  | 0.12 | 10.2733 | 0.10188
11:35 | 4004 | 23 | 259 | 10.3 | 12 | 8.154 | 0.69213 | 10.1021 |  |  |  |  | 0.13 | 10.4412 | 0.10357 |  | 0.20881
11:35 | 4012 | 23 | 259.1 | 10.3 | 13 | 8.1547 | 0.692 | 10.2733 |  |  |  |  | 0.14 | 10.6059 | 0.10524
11:35 | 4024 | 25 | 259.1 | 10.3 | 14 | 8.5019 | 0.692 | 10.4412 |  |  |  |  | 0.15 | 10.7675 | 0.10687 |  | 0.21534
11:35 | 4024 | 26 | 259 | 10.3 | 15 | 8.6695 | 0.69213 | 10.6059 |  |  |  |  | 0.16 | 10.9259 | 0.10847
11:35 | 4036 | 27 | 259 | 10.3 | 16 | 8.8346 | 0.69213 | 10.7675 |  |  |  |  | 0.17 | 11.0811 | 0.11003 |  | 0.22161
11:35 | 4036 | 28 | 259 | 10.3 | 17 | 8.9967 | 0.69213 | 10.9259 |  |  |  |  | 0.18 | 11.2333 | 0.11157
11:35 | 4051 | 29 | 259 | 10.3 | 18 | 9.156 | 0.69213 | 11.0811 |  |  |  |  | 0.19 | 11.3823 | 0.11308 |  | 0.22764
11:35 | 4054 | 32 | 259 | 10.3 | 19 | 9.6179 | 0.69213 | 11.2333 |  |  |  |  | 0.2 | 11.5284 | 0.11455
11:35 | 4062 | 32 | 259 | 10.3 | 20 | 9.6179 | 0.69213 | 11.3823 |  |  |  |  | 0.21 | 11.6714 | 0.116 |  | 0.23342
11:35 | 4068 | 36 | 259 | 10.3 | 21 | 10.2013 | 0.69213 | 11.5284 |  |  |  |  | 0.22 | 11.8114 | 0.11741
11:35 | 4071 | 36 | 259 | 10.3 | 22 | 10.2013 | 0.69213 | 11.6714 |  |  |  |  | 0.23 | 11.9484 | 0.1188 |  | 0.23896
11:35 | 4077 | 40 | 259 | 10.3 | 23 | 10.7531 | 0.69213 | 11.8114 |  |  |  |  | 0.24 | 12.0825 | 0.12015
11:35 | 4078 | 41 | 258.9 | 10.3 | 24 | 10.8857 | 0.69226 | 11.9484 |  |  |  |  | 0.25 | 12.2137 | 0.12148 |  | 0.24426
11:35 | 4088 | 42 | 258.9 | 10.3 | 25 | 11.0177 | 0.69226 | 12.0825 |  |  |  |  | 0.26 | 12.342 | 0.12278
11:35 | 4088 | 43 | 259.3 | 10.3 | 26 | 11.1522 | 0.69174 | 12.2137 |  |  |  |  | 0.27 | 12.4674 | 0.12405 |  | 0.24934
11:35 | 4088 | 43 | 259.3 | 10.3 | 27 | 11.1522 | 0.69174 | 12.342 |  |  |  |  | 0.28 | 12.59 | 0.12529
11:35 | 4088 | 44 | 259.5 | 10.3 | 28 | 11.2833 | 0.69148 | 12.4674 |  |  |  |  | 0.29 | 12.7097 | 0.1265 |  | 0.25419
11:35 | 4086 | 44 | 259.5 | 10.3 | 29 | 11.2833 | 0.69148 | 12.59 |  |  |  |  | 0.3 | 12.8267 | 0.12768
11:35 | 4084 | 45 | 259.7 | 10.3 | 30 | 11.4129 | 0.69122 | 12.7097 |  |  |  |  | 0.31 | 12.941 | 0.12884 |  | 0.25881
11:35 | 4081 | 45 | 259.8 | 10.3 | 31 | 11.414 | 0.69109 | 12.8267 |  |  |  |  | 0.32 | 13.0525 | 0.12997
11:35 | 4076 | 45 | 259.8 | 10.3 | 32 | 11.414 | 0.69109 | 12.941 |  |  |  |  | 0.33 | 13.1613 | 0.13107 |  | 0.26322
11:35 | 4075 | 44 | 259.7 | 10.3 | 33 | 11.2854 | 0.69122 | 13.0525 |  |  |  |  | 0.34 | 13.2674 | 0.13214
11:35 | 4059 | 45 | 259.8 | 10.3 | 34 | 11.414 | 0.69109 | 13.1613 |  |  |  |  | 0.35 | 13.3709 | 0.13319 |  | 0.26741
11:35 | 4059 | 45 | 259.8 | 10.3 | 35 | 11.414 | 0.69109 | 13.2674 |  |  |  |  | 0.36 | 13.4718 | 0.13421
11:35 | 4060 | 46 | 259.8 | 10.3 | 36 | 11.5401 | 0.69109 | 13.3709 |  |  |  |  | 0.37 | 13.57 | 0.13521 |  | 0.27139
11:35 | 4060 | 47 | 259.7 | 10.3 | 37 | 11.6638 | 0.69122 | 13.4718 |  |  |  |  | 0.38 | 13.6657 | 0.13618
11:35 | 4067 | 47 | 259.6 | 10.3 | 38 | 11.6627 | 0.69135 | 13.57 |  |  |  |  | 0.39 | 13.7588 | 0.13712 |  | 0.27517
11:35 | 4072 | 53 | 259.7 | 10.3 | 39 | 12.3859 | 0.69122 | 13.6657 |  |  |  |  | 0.4 | 13.8495 | 0.13804
11:35 | 4068 | 53 | 259.7 | 10.3 | 40 | 12.3859 | 0.69122 | 13.7588 |  |  |  |  | 0.41 | 13.9376 | 0.13894 |  | 0.27874
11:35 | 4057 | 54 | 259.7 | 10.3 | 41 | 12.5022 | 0.69122 | 13.8495 |  |  |  |  | 0.42 | 14.0233 | 0.1398
11:35 | 4057 | 55 | 259.7 | 10.3 | 42 | 12.6175 | 0.69122 | 13.9376 |  |  |  |  | 0.43 | 14.1065 | 0.14065 |  | 0.28212
11:35 | 4044 | 58 | 259.7 | 10.3 | 43 | 12.957 | 0.69122 | 14.0233 |  |  |  |  | 0.44 | 14.1874 | 0.14147
11:35 | 4044 | 60 | 259.7 | 10.3 | 44 | 13.1785 | 0.69122 | 14.1065 |  |  |  |  | 0.45 | 14.2658 | 0.14227 |  | 0.28531
11:35 | 4032 | 60 | 259.7 | 10.4 | 45 | 13.1785 | 0.69122 | 14.1874 |  |  |  |  | 0.46 | 14.3419 | 0.14304
11:35 | 4027 | 62 | 259.7 | 10.4 | 46 | 13.3964 | 0.69122 | 14.2658 |  |  |  |  | 0.47 | 14.4157 | 0.14379 |  | 0.28831
11:35 | 4017 | 62 | 259.7 | 10.4 | 47 | 13.3964 | 0.69122 | 14.3419 |  |  |  |  | 0.48 | 14.4871 | 0.14451
11:35 | 4007 | 58 | 259.7 | 10.4 | 48 | 12.957 | 0.69122 | 14.4157 |  |  |  |  | 0.49 | 14.5563 | 0.14522 |  | 0.29112
11:35 | 4008 | 58 | 259.7 | 10.4 | 49 | 12.957 | 0.69122 | 14.4871 |  |  |  |  | 0.5 | 14.6232 | 0.1459
11:35 | 4012 | 54 | 259.8 | 10.4 | 50 | 12.5034 | 0.69109 | 14.5563 |  |  |  |  | 0.51 | 14.6879 | 0.14656 |  | 0.29375
11:35 | 4012 | 52 | 259.9 | 10.4 | 51 | 12.2708 | 0.69096 | 14.6232 |  |  |  |  | 0.52 | 14.7505 | 0.14719
11:35 | 4015 | 53 | 259.9 | 10.4 | 52 | 12.3883 | 0.69096 | 14.6879 |  |  |  |  | 0.53 | 14.8108 | 0.14781 |  | 0.29621
11:35 | 4015 | 53 | 259.9 | 10.4 | 53 | 12.3883 | 0.69096 | 14.7505 |  |  |  |  | 0.54 | 14.869 | 0.1484
11:35 | 4015 | 53 | 259.9 | 10.4 | 54 | 12.3883 | 0.69096 | 14.8108 |  |  |  |  | 0.55 | 14.9251 | 0.14897 |  | 0.29849
11:35 | 4014 | 55 | 259.9 | 10.4 | 55 | 12.6198 | 0.69096 | 14.869 |  |  |  |  | 0.56 | 14.9791 | 0.14952
11:35 | 4009 | 55 | 259.8 | 10.4 | 56 | 12.6186 | 0.69109 | 14.9251 |  |  |  |  | 0.57 | 15.031 | 0.15005 |  | 0.30061
11:35 | 4003 | 59 | 259.9 | 10.4 | 57 | 13.0707 | 0.69096 | 14.9791 |  |  |  |  | 0.58 | 15.0809 | 0.15056
11:35 | 4001 | 59 | 259.9 | 10.4 | 58 | 13.0707 | 0.69096 | 15.031 |  |  |  |  | 0.59 | 15.1287 | 0.15105 |  | 0.30257
11:35 | 3995 | 55 | 259.9 | 10.4 | 59 | 12.6198 | 0.69096 | 15.0809 |  |  |  |  | 0.6 | 15.1746 | 0.15152
11:35 | 3995 | 54 | 259.9 | 10.3 | 60 | 12.5046 | 0.69096 | 15.1287 |  |  |  |  | 0.61 | 15.2186 | 0.15197 |  | 0.30437
11:35 | 3992 | 52 | 259.9 | 10.3 | 61 | 12.2708 | 0.69096 | 15.1746 |  |  |  |  | 0.62 | 15.2606 | 0.1524
11:35 | 3992 | 50 | 259.8 | 10.3 | 62 | 12.0314 | 0.69109 | 15.2186 |  |  |  |  | 0.63 | 15.3007 | 0.15281 |  | 0.30601
11:35 | 3997 | 52 | 259.8 | 10.3 | 63 | 12.2697 | 0.69109 | 15.2606 |  |  |  |  | 0.64 | 15.3389 | 0.1532
11:35 | 4000 | 59 | 259.9 | 10.3 | 64 | 13.0707 | 0.69096 | 15.3007 |  |  |  |  | 0.65 | 15.3753 | 0.15357 |  | 0.3075
11:35 | 3998 | 59 | 260 | 10.3 | 65 | 13.0719 | 0.69083 | 15.3389 |  |  |  |  | 0.66 | 15.4098 | 0.15393
11:35 | 3997 | 53 | 260 | 10.3 | 66 | 12.3894 | 0.69083 | 15.3753 |  |  |  |  | 0.67 | 15.4426 | 0.15426 |  | 0.30885
11:35 | 3989 | 53 | 260 | 10.4 | 67 | 12.3894 | 0.69083 | 15.4098 |  |  |  |  | 0.68 | 15.4736 | 0.15458
11:35 | 3966 | 55 | 260 | 10.4 | 68 | 12.621 | 0.69083 | 15.4426 |  |  |  |  | 0.69 | 15.5028 | 0.15488 |  | 0.31005
11:35 | 3964 | 56 | 260.2 | 10.4 | 69 | 12.7376 | 0.69057 | 15.4736 |  |  |  |  | 0.7 | 15.5304 | 0.15517
11:35 | 3924 | 61 | 260.2 | 10.4 | 70 | 13.2941 | 0.69057 | 15.5028 |  |  |  |  | 0.71 | 15.5562 | 0.15543 |  | 0.31112
11:36 | 3924 | 64 | 260.2 | 10.4 | 71 | 13.6171 | 0.69057 | 15.5304 |  |  |  |  | 0.72 | 15.5804 | 0.15568
11:36 | 3908 | 63 | 260.2 | 10.4 | 72 | 13.5103 | 0.69057 | 15.5562 |  |  |  |  | 0.73 | 15.6029 | 0.15592 |  | 0.31205
11:36 | 3899 | 58 | 260.3 | 10.4 | 73 | 12.9643 | 0.69044 | 15.5804 |  |  |  |  | 0.74 | 15.6238 | 0.15613
11:36 | 3903 | 58 | 260.3 | 10.4 | 74 | 12.9643 | 0.69044 | 15.6029 |  |  |  |  | 0.75 | 15.6431 | 0.15633 |  | 0.31286
11:36 | 3908 | 50 | 260.3 | 10.4 | 75 | 12.037 | 0.69044 | 15.6238 |  |  |  |  | 0.76 | 15.6609 | 0.15652
11:36 | 3909 | 50 | 260.2 | 10.4 | 76 | 12.0359 | 0.69057 | 15.6431 |  |  |  |  | 0.77 | 15.6772 | 0.15669 |  | 0.31354
11:36 | 3916 | 48 | 260.2 | 10.4 | 77 | 11.7927 | 0.69057 | 15.6609 |  |  |  |  | 0.78 | 15.6919 | 0.15685
11:36 | 3917 | 47 | 260.1 | 10.4 | 78 | 11.6682 | 0.6907 | 15.6772 |  |  |  |  | 0.79 | 15.7052 | 0.15699 |  | 0.3141
11:36 | 3928 | 50 | 260.1 | 10.4 | 79 | 12.0348 | 0.6907 | 15.6919 |  |  |  |  | 0.8 | 15.717 | 0.15711
11:36 | 3928 | 52 | 260.2 | 10.4 | 80 | 12.2743 | 0.69057 | 15.7052 |  |  |  |  | 0.81 | 15.7274 | 0.15722 |  | 0.31454
11:36 | 3931 | 52 | 260.2 | 10.4 | 81 | 12.2743 | 0.69057 | 15.717 |  |  |  |  | 0.82 | 15.7364 | 0.15732
11:36 | 3932 | 50 | 260.2 | 10.4 | 82 | 12.0359 | 0.69057 | 15.7274 |  |  |  |  | 0.83 | 15.744 | 0.1574 |  | 0.31488
11:36 | 3933 | 50 | 260.2 | 10.4 | 83 | 12.0359 | 0.69057 | 15.7364 |  |  |  |  | 0.84 | 15.7503 | 0.15747
11:36 | 3934 | 47 | 260.3 | 10.4 | 84 | 11.6704 | 0.69044 | 15.744 |  |  |  |  | 0.85 | 15.7553 | 0.15753 |  | 0.3151
11:36 | 3935 | 47 | 260.3 | 10.4 | 85 | 11.6704 | 0.69044 | 15.7503 |  |  |  |  | 0.86 | 15.7589 | 0.15757
11:36 | 3937 | 50 | 260.3 | 10.4 | 86 | 12.037 | 0.69044 | 15.7553 |  |  |  |  | 0.87 | 15.7613 | 0.1576 |  | 0.31522
11:36 | 3937 | 52 | 260.1 | 10.4 | 87 | 12.2731 | 0.6907 | 15.7589 |  |  |  |  | 0.88 | 15.7625 | 0.15762
11:36 | 3939 | 55 | 260.2 | 10.4 | 88 | 12.6234 | 0.69057 | 15.7613 |  |  |  |  | 0.89 | 15.7625 | 0.15762 |  | 0.31525
11:36 | 3939 | 57 | 260.6 | 10.4 | 89 | 12.8557 | 0.69006 | 15.7625 |  |  |  |  | 0.9 | 15.7612 | 0.15762
11:36 | 3941 | 57 | 260.6 | 10.4 | 90 | 12.8557 | 0.69006 | 15.7625 |  |  |  |  | 0.91 | 15.7589 | 0.1576 |  | 0.31517
11:36 | 3942 | 57 | 260.4 | 10.4 | 91 | 12.8533 | 0.69031 | 15.7612 |  |  |  |  | 0.92 | 15.7553 | 0.15757
11:36 | 3941 | 56 | 260.2 | 10.4 | 92 | 12.7376 | 0.69057 | 15.7589 |  |  |  |  | 0.93 | 15.7507 | 0.15753 |  | 0.31501
11:36 | 3940 | 50 | 260.3 | 10.4 | 93 | 12.037 | 0.69044 | 15.7553 |  |  |  |  | 0.94 | 15.745 | 0.15748
11:36 | 3938 | 50 | 260.4 | 10.4 | 94 | 12.0382 | 0.69031 | 15.7507 |  |  |  |  | 0.95 | 15.7383 | 0.15742 |  | 0.31476
11:36 | 3926 | 50 | 260.4 | 10.4 | 95 | 12.0382 | 0.69031 | 15.745 |  |  |  |  | 0.96 | 15.7305 | 0.15734
11:36 | 3926 | 51 | 260.4 | 10.4 | 96 | 12.158 | 0.69031 | 15.7383 |  |  |  |  | 0.97 | 15.7217 | 0.15726 |  | 0.31443
11:36 | 3912 | 48 | 260.4 | 10.3 | 97 | 11.795 | 0.69031 | 15.7305 |  |  |  |  | 0.98 | 15.712 | 0.15717
11:36 | 3912 | 45 | 260.7 | 10.3 | 98 | 11.4236 | 0.68993 | 15.7217 |  |  |  |  | 0.99 | 15.7013 | 0.15707 |  | 0.31402
11:36 | 3914 | 45 | 260.7 | 10.3 | 99 | 11.4236 | 0.68993 | 15.712 |  |  |  |  | 1 | 15.6897 | 0.15696
11:36 | 3916 | 45 | 260.7 | 10.3 | 100 | 11.4236 | 0.68993 | 15.7013 |  |  |  |  | 0 | 15.6772 | -15.6835 |  | -15.5203
11:36 | 3920 | 45 | 260.8 | 10.3 | 101 | 11.4247 | 0.6898 | 15.6897 |  |  |  |  | 0.01 | 15.6639 | 0.15671
11:36 | 3924 | 46 | 260.9 | 10.3 | 102 | 11.552 | 0.68967 | 15.6772 |  |  |  |  | 0.02 | 15.6497 | 0.15657 |  | 0.31299
11:36 | 3924 | 46 | 261 | 10.3 | 103 | 11.5531 | 0.68954 | 15.6639 |  |  |  |  | 0.03 | 15.6347 | 0.15642
11:36 | 3927 | 43 | 261 | 10.3 | 104 | 11.17 | 0.68954 | 15.6497 |  |  |  |  | 0.04 | 15.6189 | 0.15627 |  | 0.31237
11:36 | 3927 | 41 | 261 | 10.3 | 105 | 10.9072 | 0.68954 | 15.6347 |  |  |  |  | 0.05 | 15.6023 | 0.15611
11:36 | 3931 | 40 | 261.1 | 10.3 | 106 | 10.7743 | 0.68941 | 15.6189 |  |  |  |  | 0.06 | 15.585 | 0.15594 |  | 0.3117
11:36 | 3931 | 40 | 261.2 | 10.3 | 107 | 10.7753 | 0.68928 | 15.6023 |  |  |  |  | 0.07 | 15.567 | 0.15576
11:36 | 3932 | 40 | 261.2 | 10.3 | 108 | 10.7753 | 0.68928 | 15.585 |  |  |  |  | 0.08 | 15.5484 | 0.15558 |  | 0.31097
11:36 | 3933 | 43 | 261.2 | 10.3 | 109 | 11.1721 | 0.68928 | 15.567 |  |  |  |  | 0.09 | 15.5291 | 0.15539
11:36 | 3942 | 42 | 261.3 | 10.3 | 110 | 11.0425 | 0.68915 | 15.5484 |  |  |  |  | 0.1 | 15.5091 | 0.15519 |  | 0.31018
11:36 | 3951 | 42 | 261.2 | 10.3 | 111 | 11.0414 | 0.68928 | 15.5291 |  |  |  |  | 0.11 | 15.4886 | 0.15499
11:36 | 3952 | 42 | 261.2 | 10.3 | 112 | 11.0414 | 0.68928 | 15.5091 |  |  |  |  | 0.12 | 15.4675 | 0.15478 |  | 0.30935
11:36 | 3962 | 43 | 261.2 | 10.3 | 113 | 11.1721 | 0.68928 | 15.4886 |  |  |  |  | 0.13 | 15.4458 | 0.15457
11:36 | 3962 | 44 | 261.5 | 10.3 | 114 | 11.3044 | 0.68889 | 15.4675 |  |  |  |  | 0.14 | 15.4236 | 0.15435 |  | 0.30847
11:36 | 3963 | 44 | 261.5 | 10.3 | 115 | 11.3044 | 0.68889 | 15.4458 |  |  |  |  | 0.15 | 15.401 | 0.15412
11:36 | 3963 | 44 | 261.6 | 10.3 | 116 | 11.3055 | 0.68877 | 15.4236 |  |  |  |  | 0.16 | 15.3779 | 0.15389 |  | 0.30756
11:36 | 3961 | 44 | 261.6 | 10.3 | 117 | 11.3055 | 0.68877 | 15.401 |  |  |  |  | 0.17 | 15.3543 | 0.15366
11:36 | 3960 | 44 | 261.7 | 10.3 | 118 | 11.3066 | 0.68864 | 15.3779 |  |  |  |  | 0.18 | 15.3303 | 0.15342 |  | 0.3066
11:36 | 3959 | 44 | 261.7 | 10.3 | 119 | 11.3066 | 0.68864 | 15.3543 |  |  |  |  | 0.19 | 15.3059 | 0.15318
11:36 | 3958 | 44 | 261.6 | 10.3 | 120 | 11.3055 | 0.68877 | 15.3303 |  |  |  |  | 0.2 | 15.2812 | 0.15294 |  | 0.30562
11:36 | 3958 | 44 | 261.6 | 10.3 | 121 | 11.3055 | 0.68877 | 15.3059 |  |  |  |  | 0.21 | 15.2562 | 0.15269
11:36 | 3961 | 44 | 261.6 | 10.3 | 122 | 11.3055 | 0.68877 | 15.2812 |  |  |  |  | 0.22 | 15.2308 | 0.15243 |  | 0.30462
11:36 | 3961 | 44 | 261.5 | 10.3 | 123 | 11.3044 | 0.68889 | 15.2562 |  |  |  |  | 0.23 | 15.2052 | 0.15218
11:36 | 3982 | 44 | 261.5 | 10.3 | 124 | 11.3044 | 0.68889 | 15.2308 |  |  |  |  | 0.24 | 15.1793 | 0.15192 |  | 0.30358
11:36 | 3982 | 43 | 261.4 | 10.3 | 125 | 11.1742 | 0.68902 | 15.2052 |  |  |  |  | 0.25 | 15.1532 | 0.15166
11:36 | 3986 | 44 | 261.4 | 10.3 | 126 | 11.3034 | 0.68902 | 15.1793 |  |  |  |  | 0.26 | 15.1268 | 0.1514 |  | 0.30254
11:36 | 3990 | 47 | 261.3 | 10.3 | 127 | 11.6813 | 0.68915 | 15.1532 |  |  |  |  | 0.27 | 15.1004 | 0.15114
11:36 | 3983 | 47 | 261.2 | 10.3 | 128 | 11.6802 | 0.68928 | 15.1268 |  |  |  |  | 0.28 | 15.0737 | 0.15087 |  | 0.30147
11:36 | 3975 | 42 | 261.1 | 10.3 | 129 | 11.0404 | 0.68941 | 15.1004 |  |  |  |  | 0.29 | 15.047 | 0.1506
11:36 | 3974 | 42 | 261 | 10.3 | 130 | 11.0394 | 0.68954 | 15.0737 |  |  |  |  | 0.3 | 15.0201 | 0.15034 |  | 0.3004
11:36 | 3956 | 40 | 261 | 10.3 | 131 | 10.7733 | 0.68954 | 15.047 |  |  |  |  | 0.31 | 14.9932 | 0.15007
11:36 | 3956 | 37 | 260.9 | 10.3 | 132 | 10.3605 | 0.68967 | 15.0201 |  |  |  |  | 0.32 | 14.9663 | 0.1498 |  | 0.29933
11:36 | 3955 | 40 | 260.9 | 10.3 | 133 | 10.7723 | 0.68967 | 14.9932 |  |  |  |  | 0.33 | 14.9393 | 0.14953
11:36 | 3955 | 43 | 261.1 | 10.3 | 134 | 11.1711 | 0.68941 | 14.9663 |  |  |  |  | 0.34 | 14.9124 | 0.14926 |  | 0.29825
11:36 | 3965 | 43 | 261.1 | 10.3 | 135 | 11.1711 | 0.68941 | 14.9393 |  |  |  |  | 0.35 | 14.8855 | 0.14899
11:36 | 3973 | 44 | 261.2 | 10.3 | 136 | 11.3013 | 0.68928 | 14.9124 |  |  |  |  | 0.36 | 14.8586 | 0.14872 |  | 0.29717
11:36 | 3984 | 44 | 261.3 | 10.3 | 137 | 11.3023 | 0.68915 | 14.8855 |  |  |  |  | 0.37 | 14.8319 | 0.14845
11:36 | 3995 | 51 | 261.3 | 10.3 | 138 | 12.1682 | 0.68915 | 14.8586 |  |  |  |  | 0.38 | 14.8053 | 0.14819 |  | 0.29611
11:36 | 3996 | 51 | 261.3 | 10.3 | 139 | 12.1682 | 0.68915 | 14.8319 |  |  |  |  | 0.39 | 14.7788 | 0.14792
11:36 | 4006 | 52 | 261.3 | 10.3 | 140 | 12.2869 | 0.68915 | 14.8053 |  |  |  |  | 0.4 | 14.7525 | 0.14766 |  | 0.29505
11:36 | 4006 | 54 | 261.2 | 10.3 | 141 | 12.5198 | 0.68928 | 14.7788 |  |  |  |  | 0.41 | 14.7264 | 0.14739
11:36 | 4007 | 53 | 261.2 | 10.3 | 142 | 12.4033 | 0.68928 | 14.7525 |  |  |  |  | 0.42 | 14.7006 | 0.14713 |  | 0.29401
11:36 | 4007 | 52 | 261.2 | 10.3 | 143 | 12.2858 | 0.68928 | 14.7264 |  |  |  |  | 0.43 | 14.675 | 0.14688
11:36 | 4005 | 52 | 261.2 | 10.3 | 144 | 12.2858 | 0.68928 | 14.7006 |  |  |  |  | 0.44 | 14.6496 | 0.14662 |  | 0.29299
11:36 | 4004 | 55 | 261.3 | 10.3 | 145 | 12.6364 | 0.68915 | 14.675 |  |  |  |  | 0.45 | 14.6246 | 0.14637
11:36 | 4001 | 55 | 261.3 | 10.3 | 146 | 12.6364 | 0.68915 | 14.6496 |  |  |  |  | 0.46 | 14.5999 | 0.14612 |  | 0.292
11:36 | 3998 | 50 | 261.4 | 10.3 | 147 | 12.0494 | 0.68902 | 14.6246 |  |  |  |  | 0.47 | 14.5756 | 0.14588
11:36 | 3997 | 49 | 261.4 | 10.3 | 148 | 11.9283 | 0.68902 | 14.5999 |  |  |  |  | 0.48 | 14.5516 | 0.14564 |  | 0.29103
11:36 | 3990 | 48 | 261.4 | 10.3 | 149 | 11.806 | 0.68902 | 14.5756 |  |  |  |  | 0.49 | 14.5281 | 0.1454
11:36 | 3990 | 47 | 261.5 | 10.3 | 150 | 11.6835 | 0.68889 | 14.5516 |  |  |  |  | 0.5 | 14.505 | 0.14517 |  | 0.2901
11:36 | 3966 | 47 | 261.5 | 10.3 | 151 | 11.6835 | 0.68889 | 14.5281 |  |  |  |  | 0.51 | 14.4824 | 0.14494
11:36 | 3965 | 47 | 261.6 | 10.3 | 152 | 11.6846 | 0.68877 | 14.505 |  |  |  |  | 0.52 | 14.4603 | 0.14471 |  | 0.28921
11:36 | 3960 | 47 | 261.6 | 10.3 | 153 | 11.6846 | 0.68877 | 14.4824 |  |  |  |  | 0.53 | 14.4387 | 0.14449
11:36 | 3955 | 48 | 261.6 | 10.3 | 154 | 11.8082 | 0.68877 | 14.4603 |  |  |  |  | 0.54 | 14.4176 | 0.14428 |  | 0.28835
11:36 | 3954 | 48 | 261.6 | 10.3 | 155 | 11.8082 | 0.68877 | 14.4387 |  |  |  |  | 0.55 | 14.3972 | 0.14407
11:36 | 3953 | 48 | 261.5 | 10.3 | 156 | 11.8071 | 0.68889 | 14.4176 |  |  |  |  | 0.56 | 14.3773 | 0.14387 |  | 0.28755
11:36 | 3954 | 48 | 261.4 | 10.3 | 157 | 11.806 | 0.68902 | 14.3972 |  |  |  |  | 0.57 | 14.358 | 0.14368
11:36 | 3970 | 49 | 261.4 | 10.3 | 158 | 11.9283 | 0.68902 | 14.3773 |  |  |  |  | 0.58 | 14.3394 | 0.14349 |  | 0.28679
11:36 | 3970 | 50 | 261.6 | 10.3 | 159 | 12.0517 | 0.68877 | 14.358 |  |  |  |  | 0.59 | 14.3215 | 0.1433
11:36 | 3994 | 49 | 261.6 | 10.3 | 160 | 11.9306 | 0.68877 | 14.3394 |  |  |  |  | 0.6 | 14.3043 | 0.14313 |  | 0.28609
11:36 | 3996 | 48 | 261.6 | 10.3 | 161 | 11.8082 | 0.68877 | 14.3215 |  |  |  |  | 0.61 | 14.2878 | 0.14296
11:36 | 3998 | 48 | 261.6 | 10.3 | 162 | 11.8082 | 0.68877 | 14.3043 |  |  |  |  | 0.62 | 14.2721 | 0.1428 |  | 0.28545
11:36 | 4000 | 47 | 261.8 | 10.3 | 163 | 11.6867 | 0.68851 | 14.2878 |  |  |  |  | 0.63 | 14.2572 | 0.14265
11:36 | 4001 | 47 | 261.9 | 10.3 | 164 | 11.6878 | 0.68838 | 14.2721 |  |  |  |  | 0.64 | 14.2431 | 0.1425 |  | 0.28486
11:36 | 4001 | 46 | 262 | 10.3 | 165 | 11.5639 | 0.68825 | 14.2572 |  |  |  |  | 0.65 | 14.2298 | 0.14236
11:36 | 4001 | 46 | 262.1 | 10.3 | 166 | 11.565 | 0.68812 | 14.2431 |  |  |  |  | 0.66 | 14.2174 | 0.14224 |  | 0.28435
11:36 | 3992 | 49 | 262.1 | 10.3 | 167 | 11.9362 | 0.68812 | 14.2298 |  |  |  |  | 0.67 | 14.2059 | 0.14212
11:36 | 3992 | 52 | 262.1 | 10.3 | 168 | 12.2961 | 0.68812 | 14.2174 |  |  |  |  | 0.68 | 14.1953 | 0.14201 |  | 0.28391
11:36 | 3981 | 51 | 262.1 | 10.3 | 169 | 12.1773 | 0.68812 | 14.2059 |  |  |  |  | 0.69 | 14.1857 | 0.1419
11:36 | 3980 | 49 | 262 | 10.3 | 170 | 11.935 | 0.68825 | 14.1953 |  |  |  |  | 0.7 | 14.177 | 0.14181 |  | 0.28354
11:36 | 3984 | 49 | 262 | 10.3 | 171 | 11.935 | 0.68825 | 14.1857 |  |  |  |  | 0.71 | 14.1693 | 0.14173
11:36 | 3987 | 51 | 262 | 10.3 | 172 | 12.1762 | 0.68825 | 14.177 |  |  |  |  | 0.72 | 14.1627 | 0.14166 |  | 0.28326
11:36 | 3990 | 51 | 262 | 10.3 | 173 | 12.1762 | 0.68825 | 14.1693 |  |  |  |  | 0.73 | 14.1571 | 0.1416
11:36 | 3993 | 52 | 262 | 10.3 | 174 | 12.295 | 0.68825 | 14.1627 |  |  |  |  | 0.74 | 14.1526 | 0.14155 |  | 0.28306
11:36 | 3993 | 52 | 261.9 | 10.3 | 175 | 12.2938 | 0.68838 | 14.1571 |  |  |  |  | 0.75 | 14.1492 | 0.14151
11:36 | 3994 | 55 | 261.9 | 10.3 | 176 | 12.6435 | 0.68838 | 14.1526 |  |  |  |  | 0.76 | 14.1469 | 0.14148 |  | 0.28294
11:36 | 3994 | 58 | 262.1 | 10.3 | 177 | 12.9861 | 0.68812 | 14.1492 |  |  |  |  | 0.77 | 14.1458 | 0.14146
11:36 | 3979 | 58 | 262.1 | 10.3 | 178 | 12.9861 | 0.68812 | 14.1469 |  |  |  |  | 0.78 | 14.1459 | 0.14146 |  | 0.28292
11:36 | 3977 | 59 | 261.7 | 10.3 | 179 | 13.0927 | 0.68864 | 14.1458 |  |  |  |  | 0.79 | 14.1472 | 0.14147
11:36 | 3967 | 59 | 261.7 | 10.3 | 180 | 13.0927 | 0.68864 | 14.1459 |  |  |  |  | 0.8 | 14.1497 | 0.14148 |  | 0.283
11:36 | 3958 | 58 | 261.6 | 10.3 | 181 | 12.9801 | 0.68877 | 14.1472 |  |  |  |  | 0.81 | 14.1535 | 0.14152
11:36 | 3957 | 58 | 261.6 | 10.3 | 182 | 12.9801 | 0.68877 | 14.1497 |  |  |  |  | 0.82 | 14.1586 | 0.14156 |  | 0.28318
11:36 | 3956 | 55 | 261.7 | 10.3 | 183 | 12.6411 | 0.68864 | 14.1535 |  |  |  |  | 0.83 | 14.165 | 0.14162
11:36 | 3957 | 55 | 261.8 | 10.4 | 184 | 12.6423 | 0.68851 | 14.1586 |  |  |  |  | 0.84 | 14.1728 | 0.14169 |  | 0.28346
11:36 | 3965 | 57 | 261.8 | 10.4 | 185 | 12.8701 | 0.68851 | 14.165 |  |  |  |  | 0.85 | 14.1819 | 0.14177
11:36 | 3965 | 58 | 261.8 | 10.4 | 186 | 12.9825 | 0.68851 | 14.1728 |  |  |  |  | 0.86 | 14.1925 | 0.14187 |  | 0.28385
11:36 | 3960 | 59 | 261.8 | 10.4 | 187 | 13.0939 | 0.68851 | 14.1819 |  |  |  |  | 0.87 | 14.2044 | 0.14198
11:36 | 3958 | 60 | 261.7 | 10.4 | 188 | 13.2032 | 0.68864 | 14.1925 |  |  |  |  | 0.88 | 14.2179 | 0.14211 |  | 0.28436
11:36 | 3960 | 60 | 261.7 | 10.4 | 189 | 13.2032 | 0.68864 | 14.2044 |  |  |  |  | 0.89 | 14.2328 | 0.14225
11:36 | 3961 | 57 | 261.6 | 10.4 | 190 | 12.8677 | 0.68877 | 14.2179 |  |  |  |  | 0.9 | 14.2492 | 0.14241 |  | 0.28499
11:36 | 3968 | 57 | 261.5 | 10.4 | 191 | 12.8665 | 0.68889 | 14.2328 |  |  |  |  | 0.91 | 14.2671 | 0.14258
11:36 | 3977 | 53 | 261.5 | 10.4 | 192 | 12.4068 | 0.68889 | 14.2492 |  |  |  |  | 0.92 | 14.2866 | 0.14277 |  | 0.28574
11:36 | 3978 | 53 | 261.6 | 10.4 | 193 | 12.408 | 0.68877 | 14.2671 |  |  |  |  | 0.93 | 14.3077 | 0.14297
11:36 | 3986 | 50 | 261.6 | 10.3 | 194 | 12.0517 | 0.68877 | 14.2866 |  |  |  |  | 0.94 | 14.3304 | 0.14319 |  | 0.28661
11:36 | 3986 | 47 | 261.7 | 10.3 | 195 | 11.6856 | 0.68864 | 14.3077 |  |  |  |  | 0.95 | 14.3547 | 0.14343
11:36 | 3994 | 48 | 261.7 | 10.3 | 196 | 11.8093 | 0.68864 | 14.3304 |  |  |  |  | 0.96 | 14.3807 | 0.14368 |  | 0.28762
11:36 | 3996 | 51 | 261.9 | 10.3 | 197 | 12.175 | 0.68838 | 14.3547 |  |  |  |  | 0.97 | 14.4084 | 0.14395
11:36 | 3993 | 51 | 262 | 10.3 | 198 | 12.1762 | 0.68825 | 14.3807 |  |  |  |  | 0.98 | 14.4378 | 0.14423 |  | 0.28876
11:36 | 3991 | 51 | 261.8 | 10.4 | 199 | 12.1739 | 0.68851 | 14.4084 |  |  |  |  | 0.99 | 14.469 | 0.14453
11:36 | 3987 | 51 | 261.7 | 10.4 | 200 | 12.1728 | 0.68864 | 14.4378 |  |  |  |  | 1 | 14.5019 | 0.14485
11:36 | 3980 | 53 | 261.7 | 10.4 | 201 | 12.4091 | 0.68864 | 14.469
11:36 | 3979 | 54 | 261.8 | 10.4 | 202 | 12.5268 | 0.68851 | 14.5019
11:36 | 3978 | 55 | 261.8 | 10.4 | 203 | 12.6423 | 0.68851 | 14.5367
11:36 | 3978 | 56 | 261.8 | 10.4 | 204 | 12.7567 | 0.68851 | 14.5732
11:36 | 3967 | 55 | 261.8 | 10.4 | 205 | 12.6423 | 0.68851 | 14.6117
11:36 | 3964 | 52 | 261.6 | 10.4 | 206 | 12.2904 | 0.68877 | 14.652
11:36 | 3960 | 52 | 261.6 | 10.4 | 207 | 12.2904 | 0.68877 | 14.6942
11:36 | 3956 | 47 | 261.8 | 10.4 | 208 | 11.6867 | 0.68851 | 14.7383
11:36 | 3956 | 47 | 262 | 10.4 | 209 | 11.6889 | 0.68825 | 14.7844
11:36 | 3955 | 45 | 261.9 | 10.4 | 210 | 11.4365 | 0.68838 | 14.8325
11:36 | 3954 | 45 | 261.8 | 10.4 |  | 11.4354 | 0.68851
11:36 | 3947 | 41 | 261.8 | 10.4 |  | 10.9153 | 0.68851
11:36 | 3947 | 37 | 261.7 | 10.4 |  | 10.3682 | 0.68864
11:36 | 3945 | 38 | 261.7 | 10.4 |  | 10.5074 | 0.68864
11:36 | 3944 | 41 | 261.7 | 10.4 |  | 10.9143 | 0.68864
11:36 | 3943 | 41 | 261.7 | 10.4 |  | 10.9143 | 0.68864
11:36 | 3942 | 43 | 261.8 | 10.4 |  | 11.1784 | 0.68851
11:36 | 3942 | 43 | 261.9 | 10.4 |  | 11.1794 | 0.68838
11:36 | 3942 | 43 | 261.9 | 10.4 |  | 11.1794 | 0.68838
11:36 | 3943 | 43 | 261.8 | 10.4 |  | 11.1784 | 0.68851
11:36 | 3954 | 40 | 261.8 | 10.4 |  | 10.7814 | 0.68851
11:36 | 3954 | 37 | 261.9 | 10.4 |  | 10.3702 | 0.68838
11:36 | 3962 | 37 | 261.9 | 10.4 |  | 10.3702 | 0.68838
11:36 | 3964 | 38 | 262 | 10.4 |  | 10.5104 | 0.68825
11:36 | 3966 | 38 | 262 | 10.4 |  | 10.5104 | 0.68825
11:36 | 3967 | 29 | 261.9 | 10.4 |  | 9.1809 | 0.68838
11:36 | 3967 | 29 | 261.8 | 10.4 |  | 9.18 | 0.68851
11:36 | 3969 | 26 | 261.9 | 10.4 |  | 8.693 | 0.68838
11:36 | 3969 | 25 | 262 | 10.4 |  | 8.525 | 0.68825
11:36 | 3965 | 25 | 262 | 10.4 |  | 8.525 | 0.68825
11:36 | 3965 | 26 | 261.8 | 10.4 |  | 8.6922 | 0.68851
11:36 | 3975 | 26 | 261.8 | 10.3 |  | 8.6922 | 0.68851
11:36 | 3979 | 26 | 261.9 | 10.3 |  | 8.693 | 0.68838
11:36 | 3976 | 26 | 261.9 | 10.4 |  | 8.693 | 0.68838
11:36 | 3974 | 26 | 261.9 | 10.4 |  | 8.693 | 0.68838
11:36 | 3973 | 26 | 261.9 | 10.4 |  | 8.693 | 0.68838
11:36 | 3969 | 30 | 261.9 | 10.4 |  | 9.3378 | 0.68838
11:36 | 3969 | 31 | 261.7 | 10.4 |  | 9.4904 | 0.68864
11:36 | 3965 | 33 | 261.7 | 10.4 |  | 9.7918 | 0.68864
11:36 | 3965 | 34 | 261.6 | 10.3 |  | 9.9381 | 0.68877
11:36 | 3952 | 34 | 261.6 | 10.3 |  | 9.9381 | 0.68877
11:36 | 3947 | 34 | 261.8 | 10.3 |  | 9.9399 | 0.68851
11:36 | 3950 | 34 | 262 | 10.3 |  | 9.9418 | 0.68825
11:36 | 3952 | 34 | 262.1 | 10.3 |  | 9.9427 | 0.68812
11:36 | 3957 | 34 | 262.2 | 10.3 |  | 9.9437 | 0.68799
11:36 | 3974 | 38 | 262.2 | 10.3 |  | 10.5123 | 0.68799
11:36 | 3974 | 41 | 262 | 10.3 |  | 10.9174 | 0.68825
11:36 | 3967 | 39 | 262 | 10.3 |  | 10.6478 | 0.68825
11:36 | 3967 | 39 | 261.9 | 10.3 |  | 10.6468 | 0.68838
11:36 | 3958 | 38 | 261.9 | 10.3 |  | 10.5094 | 0.68838
11:36 | 3954 | 36 | 261.9 | 10.3 |  | 10.2291 | 0.68838
11:36 | 3951 | 36 | 261.9 | 10.3 |  | 10.2291 | 0.68838
11:36 | 3949 | 30 | 261.9 | 10.3 |  | 9.3378 | 0.68838
11:36 | 3948 | 30 | 261.9 | 10.3 |  | 9.3378 | 0.68838
11:36 | 3943 | 33 | 261.9 | 10.3 |  | 9.7936 | 0.68838
11:36 | 3943 | 35 | 262.2 | 10.3 |  | 10.0888 | 0.68799
11:36 | 3949 | 34 | 262.2 | 10.3 |  | 9.9437 | 0.68799
11:36 | 3949 | 32 | 262.1 | 10.3 |  | 9.6459 | 0.68812
11:36 | 3947 | 33 | 262.1 | 10.3 |  | 9.7954 | 0.68812
11:36 | 3946 | 38 | 262.3 | 10.3 |  | 10.5133 | 0.68786
11:36 | 3940 | 38 | 262.4 | 10.3 |  | 10.5143 | 0.68774
11:36 | 3934 | 34 | 262.5 | 10.3 |  | 9.9464 | 0.68761
11:36 | 3934 | 34 | 262.6 | 10.3 |  | 9.9474 | 0.68748
11:36 | 3934 | 37 | 262.6 | 10.3 |  | 10.377 | 0.68748
11:36 | 3934 | 39 | 262.5 | 10.3 |  | 10.6527 | 0.68761
11:36 | 3934 | 43 | 262.5 | 10.3 |  | 11.1857 | 0.68761
11:36 | 3934 | 47 | 262.4 | 10.3 |  | 11.6933 | 0.68774
11:36 | 3935 | 47 | 262.4 | 10.3 |  | 11.6933 | 0.68774
11:36 | 3935 | 46 | 262.5 | 10.3 |  | 11.5693 | 0.68761
11:36 | 3944 | 46 | 262.5 | 10.3 |  | 11.5693 | 0.68761
11:36 | 3951 | 45 | 262.5 | 10.3 |  | 11.4429 | 0.68761
11:36 | 3952 | 45 | 262.5 | 10.3 |  | 11.4429 | 0.68761
11:36 | 3953 | 45 | 262.5 | 10.3 |  | 11.4429 | 0.68761
11:36 | 3954 | 45 | 262.5 | 10.3 |  | 11.4429 | 0.68761
11:36 | 3962 | 45 | 262.5 | 10.2 |  | 11.4429 | 0.68761
11:36 | 3962 | 45 | 262.6 | 10.2 |  | 11.4439 | 0.68748
11:36 | 3971 | 45 | 262.6 | 10.2 |  | 11.4439 | 0.68748
11:36 | 3977 | 45 | 262.5 | 10.2 |  | 11.4429 | 0.68761
11:36 | 3987 | 45 | 262.5 | 10.2 |  | 11.4429 | 0.68761
11:36 | 3996 | 45 | 262.5 | 10.2 |  | 11.4429 | 0.68761
11:36 | 3998 | 45 | 262.4 | 10.3 |  | 11.4418 | 0.68774
11:36 | 4022 | 47 | 262.4 | 10.3 |  | 11.6933 | 0.68774
11:36 | 4022 | 49 | 262.4 | 10.3 |  | 11.9395 | 0.68774
11:36 | 4021 | 54 | 262.4 | 10.3 |  | 12.5339 | 0.68774
11:36 | 4021 | 59 | 262.4 | 10.3 |  | 13.1013 | 0.68774
11:36 | 4014 | 59 | 262.4 | 10.4 |  | 13.1013 | 0.68774
11:36 | 4008 | 52 | 262.4 | 10.4 |  | 12.2996 | 0.68774
11:36 | 4008 | 52 | 262.4 | 10.4 |  | 12.2996 | 0.68774
11:36 | 4007 | 54 | 262.3 | 10.4 |  | 12.5327 | 0.68786
11:36 | 4007 | 54 | 262.3 | 10.4 |  | 12.5327 | 0.68786
11:36 | 3997 | 54 | 262.3 | 10.4 |  | 12.5327 | 0.68786
11:36 | 3997 | 53 | 262.3 | 10.4 |  | 12.4161 | 0.68786
11:36 | 3998 | 53 | 262.3 | 10.4 |  | 12.4161 | 0.68786
11:36 | 3998 | 53 | 262.2 | 10.4 |  | 12.4149 | 0.68799
11:36 | 3996 | 53 | 262.2 | 10.4 |  | 12.4149 | 0.68799
11:36 | 3994 | 55 | 262.3 | 10.4 |  | 12.6482 | 0.68786
11:36 | 3990 | 55 | 262.4 | 10.3 |  | 12.6494 | 0.68774
11:36 | 3985 | 56 | 262.5 | 10.3 |  | 12.765 | 0.68761
11:36 | 3985 | 56 | 262.6 | 10.4 |  | 12.7662 | 0.68748
11:36 | 3976 | 56 | 262.6 | 10.4 |  | 12.7662 | 0.68748
11:36 | 3976 | 56 | 262.7 | 10.4 |  | 12.7674 | 0.68735
11:36 | 3962 | 55 | 262.7 | 10.4 |  | 12.6529 | 0.68735
11:36 | 3962 | 54 | 262.5 | 10.4 |  | 12.535 | 0.68761
11:36 | 3956 | 53 | 262.5 | 10.4 |  | 12.4184 | 0.68761
11:36 | 3951 | 50 | 262.7 | 10.4 |  | 12.0641 | 0.68735
11:36 | 3954 | 50 | 262.8 | 10.4 |  | 12.0652 | 0.68722
11:36 | 3957 | 50 | 262.8 | 10.4 |  | 12.0652 | 0.68722
11:36 | 3957 | 50 | 262.8 | 10.4 |  | 12.0652 | 0.68722
11:36 | 3961 | 48 | 262.8 | 10.4 |  | 11.8214 | 0.68722
11:36 | 3961 | 47 | 262.9 | 10.4 |  | 11.6987 | 0.6871
11:36 | 3966 | 49 | 262.9 | 10.4 |  | 11.9451 | 0.6871
11:36 | 3966 | 52 | 262.6 | 10.4 |  | 12.3019 | 0.68748
11:36 | 3962 | 52 | 262.6 | 10.4 |  | 12.3019 | 0.68748
11:36 | 3959 | 51 | 262.7 | 10.4 |  | 12.1841 | 0.68735
11:36 | 3957 | 51 | 262.7 | 10.4 |  | 12.1841 | 0.68735
11:36 | 3955 | 50 | 262.8 | 10.4 |  | 12.0652 | 0.68722
11:36 | 3956 | 50 | 262.8 | 10.4 |  | 12.0652 | 0.68722
11:36 | 3969 | 48 | 262.8 | 10.4 |  | 11.8214 | 0.68722
11:36 | 3969 | 47 | 262.7 | 10.4 |  | 11.6966 | 0.68735
11:36 | 3987 | 49 | 262.7 | 10.4 |  | 11.9428 | 0.68735
11:36 | 3989 | 53 | 262.6 | 10.4 |  | 12.4196 | 0.68748
11:36 | 3991 | 53 | 262.6 | 10.4 |  | 12.4196 | 0.68748
11:36 | 3993 | 53 | 262.6 | 10.4 |  | 12.4196 | 0.68748
11:36 | 3991 | 53 | 262.6 | 10.3 |  | 12.4196 | 0.68748
11:36 | 3988 | 50 | 262.6 | 10.3 |  | 12.063 | 0.68748
11:36 | 3988 | 50 | 262.5 | 10.3 |  | 12.0618 | 0.68761
11:36 | 3982 | 50 | 262.5 | 10.4 |  | 12.0618 | 0.68761
11:36 | 3982 | 50 | 262.2 | 10.3 |  | 12.0585 | 0.68799
11:36 | 3978 | 49 | 262.2 | 10.3 |  | 11.9373 | 0.68799
11:36 | 3978 | 47 | 262.3 | 10.3 |  | 11.6922 | 0.68786
11:36 | 3977 | 47 | 262.3 | 10.3 |  | 11.6922 | 0.68786
11:36 | 3976 | 51 | 262.4 | 10.3 |  | 12.1807 | 0.68774
11:36 | 3971 | 51 | 262.6 | 10.3 |  | 12.183 | 0.68748
11:36 | 3964 | 53 | 262.7 | 10.3 |  | 12.4207 | 0.68735
11:36 | 3964 | 53 | 262.8 | 10.4 |  | 12.4219 | 0.68722
11:36 | 3961 | 51 | 262.8 | 10.4 |  | 12.1853 | 0.68722
11:36 | 3961 | 50 | 262.8 | 10.4 |  | 12.0652 | 0.68722
11:36 | 3959 | 50 | 262.8 | 10.4 |  | 12.0652 | 0.68722
11:36 | 3959 | 51 | 263 | 10.4 |  | 12.1875 | 0.68697
11:36 | 3961 | 51 | 263 | 10.4 |  | 12.1875 | 0.68697
11:36 | 3963 | 48 | 263 | 10.4 |  | 11.8237 | 0.68697
11:36 | 3969 | 48 | 263 | 10.3 |  | 11.8237 | 0.68697
11:36 | 3976 | 48 | 263.1 | 10.3 |  | 11.8248 | 0.68684
11:36 | 3976 | 49 | 263.2 | 10.3 |  | 11.9484 | 0.68671
11:36 | 3977 | 46 | 263.2 | 10.3 |  | 11.5769 | 0.68671
11:36 | 3977 | 45 | 263 | 10.3 |  | 11.4482 | 0.68697
11:36 | 3975 | 46 | 263 | 10.3 |  | 11.5747 | 0.68697
11:36 | 3975 | 48 | 262.9 | 10.3 |  | 11.8225 | 0.6871
11:36 | 3972 | 47 | 262.9 | 10.3 |  | 11.6987 | 0.6871
11:36 | 3969 | 46 | 262.9 | 10.3 |  | 11.5736 | 0.6871
11:36 | 3969 | 46 | 262.9 | 10.4 |  | 11.5736 | 0.6871
11:36 | 3970 | 49 | 262.9 | 10.4 |  | 11.9451 | 0.6871
11:36 | 3970 | 49 | 262.9 | 10.4 |  | 11.9451 | 0.6871
11:36 | 3977 | 48 | 262.9 | 10.4 |  | 11.8225 | 0.6871
11:36 | 3977 | 47 | 262.6 | 10.4 |  | 11.6955 | 0.68748
11:36 | 3977 | 48 | 262.6 | 10.3 |  | 11.8192 | 0.68748
11:36 | 3977 | 50 | 262.5 | 10.4 |  | 12.0618 | 0.68761
11:36 | 3972 | 50 | 262.5 | 10.4 |  | 12.0618 | 0.68761
11:36 | 3967 | 52 | 262.5 | 10.4 |  | 12.3007 | 0.68761
11:36 | 3966 | 52 | 262.5 | 10.4 |  | 12.3007 | 0.68761
11:36 | 3965 | 45 | 262.5 | 10.4 |  | 11.4429 | 0.68761
11:36 | 3965 | 44 | 262.5 | 10.4 |  | 11.315 | 0.68761
11:36 | 3969 | 44 | 262.6 | 10.4 |  | 11.3161 | 0.68748
11:36 | 3969 | 44 | 262.8 | 10.3 |  | 11.3182 | 0.68722
11:36 | 3965 | 45 | 262.8 | 10.3 |  | 11.4461 | 0.68722
11:36 | 3964 | 46 | 262.6 | 10.3 |  | 11.5704 | 0.68748
11:36 | 3975 | 46 | 262.6 | 10.3 |  | 11.5704 | 0.68748
11:36 | 3984 | 47 | 262.7 | 10.3 |  | 11.6966 | 0.68735
11:36 | 3991 | 47 | 262.7 | 10.4 |  | 11.6966 | 0.68735
11:36 | 4001 | 47 | 262.7 | 10.4 |  | 11.6966 | 0.68735
11:36 | 4001 | 47 | 262.8 | 10.4 |  | 11.6977 | 0.68722
11:36 | 4010 | 47 | 262.8 | 10.4 |  | 11.6977 | 0.68722
11:36 | 4010 | 47 | 262.7 | 10.4 |  | 11.6966 | 0.68735
11:36 | 4003 | 47 | 262.7 | 10.3 |  | 11.6966 | 0.68735
11:36 | 4000 | 47 | 262.7 | 10.3 |  | 11.6966 | 0.68735
11:37 | 3990 | 47 | 262.7 | 10.3 |  | 11.6966 | 0.68735
11:37 | 3980 | 50 | 262.8 | 10.3 |  | 12.0652 | 0.68722
11:37 | 3973 | 50 | 262.8 | 10.4 |  | 12.0652 | 0.68722
11:37 | 3961 | 55 | 262.8 | 10.4 |  | 12.6541 | 0.68722
11:37 | 3960 | 57 | 262.7 | 10.4 |  | 12.8809 | 0.68735
11:37 | 3951 | 57 | 262.7 | 10.4 |  | 12.8809 | 0.68735
11:37 | 3951 | 57 | 262.7 | 10.3 |  | 12.8809 | 0.68735
11:37 | 3943 | 55 | 262.7 | 10.3 |  | 12.6529 | 0.68735
11:37 | 3940 | 48 | 262.7 | 10.3 |  | 11.8203 | 0.68735
11:37 | 3944 | 48 | 262.7 | 10.3 |  | 11.8203 | 0.68735
11:37 | 3947 | 46 | 262.7 | 10.3 |  | 11.5715 | 0.68735
11:37 | 3945 | 46 | 262.7 | 10.3 |  | 11.5715 | 0.68735
11:37 | 3941 | 49 | 262.7 | 10.3 |  | 11.9428 | 0.68735
11:37 | 3940 | 50 | 262.7 | 10.3 |  | 12.0641 | 0.68735
11:37 | 3923 | 52 | 262.7 | 10.3 |  | 12.303 | 0.68735
11:37 | 3923 | 54 | 262.6 | 10.3 |  | 12.5362 | 0.68748
11:37 | 3925 | 54 | 262.6 | 10.4 |  | 12.5362 | 0.68748
11:37 | 3926 | 53 | 262.5 | 10.4 |  | 12.4184 | 0.68761
11:37 | 3927 | 53 | 262.4 | 10.4 |  | 12.4173 | 0.68774
11:37 | 3929 | 52 | 262.4 | 10.4 |  | 12.2996 | 0.68774
11:37 | 3929 | 52 | 262.5 | 10.4 |  | 12.3007 | 0.68761
11:37 | 3931 | 49 | 262.4 | 10.4 |  | 11.9395 | 0.68774
11:37 | 3931 | 48 | 262.3 | 10.4 |  | 11.8159 | 0.68786
11:37 | 3933 | 45 | 262.3 | 10.4 |  | 11.4407 | 0.68786
11:37 | 3933 | 42 | 262.2 | 10.4 |  | 11.0518 | 0.68799
11:37 | 3935 | 44 | 262.2 | 10.4 |  | 11.3118 | 0.68799
11:37 | 3936 | 49 | 262 | 10.4 |  | 11.935 | 0.68825
11:37 | 3944 | 49 | 261.9 | 10.4 |  | 11.9339 | 0.68838
11:37 | 3952 | 49 | 262 | 10.4 |  | 11.935 | 0.68825
11:37 | 3955 | 49 | 262 | 10.4 |  | 11.935 | 0.68825
11:37 | 3962 | 51 | 262 | 10.4 |  | 12.1762 | 0.68825
11:37 | 3962 | 51 | 262 | 10.4 |  | 12.1762 | 0.68825
11:37 | 3967 | 52 | 262 | 10.4 |  | 12.295 | 0.68825
11:37 | 3967 | 52 | 261.8 | 10.4 |  | 12.2927 | 0.68851
11:37 | 3968 | 52 | 261.8 | 10.4 |  | 12.2927 | 0.68851
11:37 | 3968 | 54 | 261.7 | 10.4 |  | 12.5257 | 0.68864
11:37 | 3966 | 55 | 261.6 | 10.4 |  | 12.6399 | 0.68877
11:37 | 3965 | 58 | 261.5 | 10.4 |  | 12.9789 | 0.68889
11:37 | 3968 | 58 | 261.5 | 10.4 |  | 12.9789 | 0.68889
11:37 | 3978 | 55 | 261.5 | 10.4 |  | 12.6387 | 0.68889
11:37 | 3979 | 54 | 261.7 | 10.4 |  | 12.5257 | 0.68864
11:37 | 3986 | 54 | 261.7 | 10.4 |  | 12.5257 | 0.68864
11:37 | 3986 | 54 | 261.5 | 10.4 |  | 12.5233 | 0.68889
11:37 | 3985 | 53 | 261.5 | 10.4 |  | 12.4068 | 0.68889
11:37 | 3984 | 45 | 261.6 | 10.4 |  | 11.4332 | 0.68877
11:37 | 3993 | 45 | 261.6 | 10.4 |  | 11.4332 | 0.68877
11:37 | 4001 | 42 | 261.5 | 10.4 |  | 11.0445 | 0.68889
11:37 | 4002 | 42 | 261.5 | 10.4 |  | 11.0445 | 0.68889
11:37 | 4006 | 40 | 261.5 | 10.4 |  | 10.7784 | 0.68889
11:37 | 4006 | 39 | 261.7 | 10.4 |  | 10.6448 | 0.68864
11:37 | 4002 | 35 | 261.7 | 10.4 |  | 10.0841 | 0.68864
11:37 | 4002 | 31 | 261.9 | 10.4 |  | 9.4922 | 0.68838
11:37 | 4008 | 31 | 261.9 | 10.4 |  | 9.4922 | 0.68838
11:37 | 4012 | 32 | 261.9 | 10.4 |  | 9.6441 | 0.68838
11:37 | 3999 | 32 | 261.9 | 10.4 |  | 9.6441 | 0.68838
11:37 | 3987 | 30 | 262 | 10.4 |  | 9.3387 | 0.68825
11:37 | 3987 | 30 | 262.1 | 10.4 |  | 9.3396 | 0.68812
11:37 | 3983 | 24 | 262.1 | 10.4 |  | 8.3536 | 0.68812
11:37 | 3983 | 20 | 262 | 10.4 |  | 7.625 | 0.68825
11:37 | 3985 | 21 | 262 | 10.4 |  | 7.8133 | 0.68825

## P3
| Port | 3
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current
| Pa | Pa | Deg C | mA
Averages | 4098.6721 | 56.6005 | 267.1928 | 10.3109 | [11 empty] | 12.4134 |  | 12.3377
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current |  |  |  |  | a | b | n | h | xi | f(xi) | Aj
| Pa. | Pa | Deg C | mA |  | 12.3493 |  |  | 0 | 1 | 100 | 0.01 | 0 | 13.4728
[6 empty] | vel | dens | [5 empty] | 0.01 | 13.2537 | 0.13363 |  | 0.26545
11:23 | 4096 | 62 | 265.8 | 10.3 | 1 | 13.4728 | 0.6834 | 14.1606 |  |  |  |  | 0.02 | 13.1465 | 0.132
11:23 | 4087 | 60 | 265.8 | 10.3 | 2 | 13.2537 | 0.6834 | 14.2297 |  |  |  |  | 0.03 | 13.0346 | 0.13091 |  | 0.26069
11:23 | 4087 | 59 | 266.1 | 10.3 | 3 | 13.1465 | 0.68302 | 14.2972 |  |  |  |  | 0.04 | 12.9229 | 0.12979
11:23 | 4085 | 58 | 266.1 | 10.2 | 4 | 13.0346 | 0.68302 | 14.3632 |  |  |  |  | 0.05 | 12.9229 | 0.12923 |  | 0.25883
11:23 | 4084 | 57 | 266.2 | 10.2 | 5 | 12.9229 | 0.68289 | 14.4277 |  |  |  |  | 0.06 | 13.0346 | 0.12979
11:23 | 4085 | 57 | 266.2 | 10.2 | 6 | 12.9229 | 0.68289 | 14.4906 |  |  |  |  | 0.07 | 13.0321 | 0.13033 |  | 0.26176
11:23 | 4085 | 58 | 266.1 | 10.2 | 7 | 13.0346 | 0.68302 | 14.5521 |  |  |  |  | 0.08 | 13.3649 | 0.13199
11:23 | 4088 | 58 | 265.9 | 10.2 | 8 | 13.0321 | 0.68327 | 14.612 |  |  |  |  | 0.09 | 13.4715 | 0.13418 |  | 0.27015
11:23 | 4093 | 61 | 265.9 | 10.2 | 9 | 13.3649 | 0.68327 | 14.6704 |  |  |  |  | 0.1 | 13.7936 | 0.13633
11:23 | 4093 | 62 | 265.7 | 10.3 | 10 | 13.4715 | 0.68353 | 14.7274 |  |  |  |  | 0.11 | 14.1096 | 0.13952 |  | 0.28114
11:23 | 4106 | 65 | 265.7 | 10.3 | 11 | 13.7936 | 0.68353 | 14.7829 |  |  |  |  | 0.12 | 14.1096 | 0.1411
11:23 | 4106 | 68 | 265.8 | 10.3 | 12 | 14.1096 | 0.6834 | 14.8369 |  |  |  |  | 0.13 | 14.2091 | 0.14159 |  | 0.28419
11:23 | 4094 | 68 | 265.8 | 10.3 | 13 | 14.1096 | 0.6834 | 14.8894 |  |  |  |  | 0.14 | 14.3103 | 0.1426
11:23 | 4091 | 69 | 265.5 | 10.3 | 14 | 14.2091 | 0.68378 | 14.9405 |  |  |  |  | 0.15 | 15.3937 | 0.14852 |  | 0.30426
11:23 | 4086 | 70 | 265.4 | 10.3 | 15 | 14.3103 | 0.68391 | 14.9901 |  |  |  |  | 0.16 | 15.3923 | 0.15393
11:23 | 4080 | 81 | 265.4 | 10.3 | 16 | 15.3937 | 0.68391 | 15.0383 |  |  |  |  | 0.17 | 15.5826 | 0.15487 |  | 0.31102
11:23 | 4079 | 81 | 265.3 | 10.3 | 17 | 15.3923 | 0.68403 | 15.0851 |  |  |  |  | 0.18 | 15.584 | 0.15583
11:23 | 4078 | 83 | 265.4 | 10.3 | 18 | 15.5826 | 0.68391 | 15.1304 |  |  |  |  | 0.19 | 15.8632 | 0.15724 |  | 0.31695
11:23 | 4080 | 83 | 265.5 | 10.3 | 19 | 15.584 | 0.68378 | 15.1743 |  |  |  |  | 0.2 | 16.0481 | 0.15956
11:23 | 4104 | 86 | 265.5 | 10.3 | 20 | 15.8632 | 0.68378 | 15.2169 |  |  |  |  | 0.21 | 16.0481 | 0.16048 |  | 0.32065
11:23 | 4104 | 88 | 265.6 | 10.3 | 21 | 16.0481 | 0.68365 | 15.258 |  |  |  |  | 0.22 | 15.9551 | 0.16002
11:23 | 4104 | 88 | 265.6 | 10.3 | 22 | 16.0481 | 0.68365 | 15.2977 |  |  |  |  | 0.23 | 15.9537 | 0.15954 |  | 0.31847
11:23 | 4104 | 87 | 265.5 | 10.3 | 23 | 15.9551 | 0.68378 | 15.336 |  |  |  |  | 0.24 | 15.7707 | 0.15862
11:23 | 4094 | 87 | 265.4 | 10.3 | 24 | 15.9537 | 0.68391 | 15.373 |  |  |  |  | 0.25 | 15.7721 | 0.15771 |  | 0.31451
11:23 | 4085 | 85 | 265.5 | 10.3 | 25 | 15.7707 | 0.68378 | 15.4086 |  |  |  |  | 0.26 | 15.4927 | 0.15632
11:23 | 4081 | 85 | 265.6 | 10.3 | 26 | 15.7721 | 0.68365 | 15.4429 |  |  |  |  | 0.27 | 15.4037 | 0.15448 |  | 0.30962
11:23 | 4074 | 82 | 265.7 | 10.3 | 27 | 15.4927 | 0.68353 | 15.4757 |  |  |  |  | 0.28 | 15.7795 | 0.15592
11:23 | 4074 | 81 | 266.1 | 10.3 | 28 | 15.4037 | 0.68302 | 15.5073 |  |  |  |  | 0.29 | 16.057 | 0.15918 |  | 0.32112
11:23 | 4078 | 85 | 266.1 | 10.3 | 29 | 15.7795 | 0.68302 | 15.5375 |  |  |  |  | 0.3 | 16.3284 | 0.16193
11:23 | 4078 | 88 | 266.2 | 10.3 | 30 | 16.057 | 0.68289 | 15.5664 |  |  |  |  | 0.31 | 16.9463 | 0.16637 |  | 0.33687
11:23 | 4097 | 91 | 266.2 | 10.3 | 31 | 16.3284 | 0.68289 | 15.594 |  |  |  |  | 0.32 | 16.9463 | 0.16946
11:23 | 4101 | 98 | 266.3 | 10.3 | 32 | 16.9463 | 0.68277 | 15.6202 |  |  |  |  | 0.33 | 17.459 | 0.17203 |  | 0.34747
11:23 | 4108 | 98 | 266.3 | 10.3 | 33 | 16.9463 | 0.68277 | 15.6452 |  |  |  |  | 0.34 | 17.459 | 0.17459
11:23 | 4114 | 104 | 266.4 | 10.3 | 34 | 17.459 | 0.68264 | 15.6688 |  |  |  |  | 0.35 | 17.2919 | 0.17375 |  | 0.34612
11:23 | 4119 | 104 | 266.4 | 10.3 | 35 | 17.459 | 0.68264 | 15.6912 |  |  |  |  | 0.36 | 17.2086 | 0.1725
11:23 | 4126 | 102 | 266.5 | 10.3 | 36 | 17.2919 | 0.68251 | 15.7123 |  |  |  |  | 0.37 | 17.3781 | 0.17293 |  | 0.34783
11:23 | 4126 | 101 | 266.6 | 10.3 | 37 | 17.2086 | 0.68239 | 15.7321 |  |  |  |  | 0.38 | 17.6277 | 0.17503
11:23 | 4122 | 103 | 266.6 | 10.3 | 38 | 17.3781 | 0.68239 | 15.7506 |  |  |  |  | 0.39 | 17.4606 | 0.17544 |  | 0.34863
11:23 | 4122 | 106 | 266.5 | 10.3 | 39 | 17.6277 | 0.68251 | 15.7679 |  |  |  |  | 0.4 | 17.12 | 0.1729
11:23 | 4114 | 104 | 266.5 | 10.3 | 40 | 17.4606 | 0.68251 | 15.784 |  |  |  |  | 0.41 | 17.2054 | 0.17163 |  | 0.3466
11:23 | 4112 | 100 | 266.4 | 10.3 | 41 | 17.12 | 0.68264 | 15.7988 |  |  |  |  | 0.42 | 18.0387 | 0.17622
11:23 | 4103 | 101 | 266.4 | 10.3 | 42 | 17.2054 | 0.68264 | 15.8124 |  |  |  |  | 0.43 | 18.0387 | 0.18039 |  | 0.35996
11:23 | 4095 | 111 | 266.5 | 10.3 | 43 | 18.0387 | 0.68251 | 15.8247 |  |  |  |  | 0.44 | 17.7933 | 0.17916
11:23 | 4092 | 111 | 266.5 | 10.3 | 44 | 18.0387 | 0.68251 | 15.8359 |  |  |  |  | 0.45 | 17.7123 | 0.17753 |  | 0.35396
11:23 | 4085 | 108 | 266.5 | 10.3 | 45 | 17.7933 | 0.68251 | 15.8458 |  |  |  |  | 0.46 | 17.546 | 0.17629
11:23 | 4085 | 107 | 266.6 | 10.3 | 46 | 17.7123 | 0.68239 | 15.8546 |  |  |  |  | 0.47 | 17.3765 | 0.17461 |  | 0.34809
11:23 | 4081 | 105 | 266.6 | 10.3 | 47 | 17.546 | 0.68239 | 15.8621 |  |  |  |  | 0.48 | 17.3765 | 0.17376
11:23 | 4081 | 103 | 266.5 | 10.3 | 48 | 17.3765 | 0.68251 | 15.8685 |  |  |  |  | 0.49 | 17.2919 | 0.17334 |  | 0.34612
11:23 | 4081 | 103 | 266.5 | 10.2 | 49 | 17.3765 | 0.68251 | 15.8736 |  |  |  |  | 0.5 | 17.2919 | 0.17292
11:23 | 4080 | 102 | 266.5 | 10.2 | 50 | 17.2919 | 0.68251 | 15.8777 |  |  |  |  | 0.51 | 17.0373 | 0.17165 |  | 0.3416
11:23 | 4067 | 102 | 266.5 | 10.2 | 51 | 17.2919 | 0.68251 | 15.8805 |  |  |  |  | 0.52 | 17.0389 | 0.17038
11:23 | 4055 | 99 | 266.6 | 10.2 | 52 | 17.0373 | 0.68239 | 15.8822 |  |  |  |  | 0.53 | 16.6015 | 0.1682 |  | 0.3326
11:23 | 4052 | 99 | 266.7 | 10.3 | 53 | 17.0389 | 0.68226 | 15.8828 |  |  |  |  | 0.54 | 16.3344 | 0.16468
11:23 | 4044 | 94 | 266.6 | 10.3 | 54 | 16.6015 | 0.68239 | 15.8822 |  |  |  |  | 0.55 | 16.0629 | 0.16199 |  | 0.32155
11:23 | 4044 | 91 | 266.6 | 10.2 | 55 | 16.3344 | 0.68239 | 15.8805 |  |  |  |  | 0.56 | 15.8779 | 0.1597
11:23 | 4055 | 88 | 266.6 | 10.2 | 56 | 16.0629 | 0.68239 | 15.8777 |  |  |  |  | 0.57 | 15.7853 | 0.15832 |  | 0.31507
11:23 | 4055 | 86 | 266.5 | 10.2 | 57 | 15.8779 | 0.68251 | 15.8738 |  |  |  |  | 0.58 | 15.5014 | 0.15643
11:23 | 4066 | 85 | 266.5 | 10.2 | 58 | 15.7853 | 0.68251 | 15.8687 |  |  |  |  | 0.59 | 15.4999 | 0.15501 |  | 0.30874
11:23 | 4070 | 82 | 266.3 | 10.2 | 59 | 15.5014 | 0.68277 | 15.8626 |  |  |  |  | 0.6 | 15.12 | 0.1531
11:23 | 4074 | 82 | 266.2 | 10.2 | 60 | 15.4999 | 0.68289 | 15.8554 |  |  |  |  | 0.61 | 15.1228 | 0.15121 |  | 0.3018
11:23 | 4077 | 78 | 266.4 | 10.2 | 61 | 15.12 | 0.68264 | 15.8471 |  |  |  |  | 0.62 | 14.9276 | 0.15025
11:23 | 4079 | 78 | 266.6 | 10.2 | 62 | 15.1228 | 0.68239 | 15.8377 |  |  |  |  | 0.63 | 14.8291 | 0.14878 |  | 0.29789
11:23 | 4082 | 76 | 266.6 | 10.2 | 63 | 14.9276 | 0.68239 | 15.8273 |  |  |  |  | 0.64 | 15.1228 | 0.14976
11:23 | 4081 | 75 | 266.6 | 10.2 | 64 | 14.8291 | 0.68239 | 15.8158 |  |  |  |  | 0.65 | 15.4094 | 0.15266 |  | 0.30723
11:23 | 4077 | 78 | 266.6 | 10.2 | 65 | 15.1228 | 0.68239 | 15.8033 |  |  |  |  | 0.66 | 15.4094 | 0.15409
11:23 | 4077 | 81 | 266.5 | 10.2 | 66 | 15.4094 | 0.68251 | 15.7897 |  |  |  |  | 0.67 | 15.3097 | 0.1536 |  | 0.30652
11:23 | 4078 | 81 | 266.5 | 10.2 | 67 | 15.4094 | 0.68251 | 15.7751 |  |  |  |  | 0.68 | 15.3069 | 0.15308
11:23 | 4079 | 80 | 266.2 | 10.2 | 68 | 15.3097 | 0.68289 | 15.7595 |  |  |  |  | 0.69 | 16.0555 | 0.15681 |  | 0.31862
11:23 | 4083 | 80 | 266 | 10.3 | 69 | 15.3069 | 0.68315 | 15.7428 |  |  |  |  | 0.7 | 16.057 | 0.16056
11:23 | 4087 | 88 | 266.1 | 10.3 | 70 | 16.0555 | 0.68302 | 15.7252 |  |  |  |  | 0.71 | 15.8735 | 0.15965 |  | 0.31776
11:23 | 4087 | 88 | 266.2 | 10.3 | 71 | 16.057 | 0.68289 | 15.7065 |  |  |  |  | 0.72 | 15.778 | 0.15826
11:23 | 4086 | 86 | 266.2 | 10.3 | 72 | 15.8735 | 0.68289 | 15.6869 |  |  |  |  | 0.73 | 15.3069 | 0.15542 |  | 0.30675
11:23 | 4086 | 85 | 266 | 10.3 | 73 | 15.778 | 0.68315 | 15.6662 |  |  |  |  | 0.74 | 15.0199 | 0.15163
11:23 | 4075 | 80 | 266 | 10.3 | 74 | 15.3069 | 0.68315 | 15.6446 |  |  |  |  | 0.75 | 14.8236 | 0.14922 |  | 0.29511
11:23 | 4075 | 77 | 266.2 | 10.3 | 75 | 15.0199 | 0.68289 | 15.6221 |  |  |  |  | 0.76 | 14.2196 | 0.14522
11:23 | 4069 | 75 | 266.2 | 10.3 | 76 | 14.8236 | 0.68289 | 15.5985 |  |  |  |  | 0.77 | 14.2196 | 0.1422 |  | 0.28119
11:23 | 4066 | 69 | 266.3 | 10.3 | 77 | 14.2196 | 0.68277 | 15.5741 |  |  |  |  | 0.78 | 13.2599 | 0.1374
11:23 | 4068 | 69 | 266.3 | 10.3 | 78 | 14.2196 | 0.68277 | 15.5486 |  |  |  |  | 0.79 | 13.2599 | 0.1326 |  | 0.26664
11:23 | 4070 | 60 | 266.3 | 10.3 | 79 | 13.2599 | 0.68277 | 15.5223 |  |  |  |  | 0.8 | 13.6934 | 0.13477
11:23 | 4074 | 60 | 266.3 | 10.3 | 80 | 13.2599 | 0.68277 | 15.495 |  |  |  |  | 0.81 | 13.9019 | 0.13798 |  | 0.27873
11:23 | 4090 | 64 | 266.2 | 10.3 | 81 | 13.6934 | 0.68289 | 15.4668 |  |  |  |  | 0.82 | 14.317 | 0.14109
11:23 | 4090 | 66 | 265.9 | 10.3 | 82 | 13.9019 | 0.68327 | 15.4377 |  |  |  |  | 0.83 | 14.6205 | 0.14469 |  | 0.2914
11:23 | 4092 | 70 | 265.9 | 10.3 | 83 | 14.317 | 0.68327 | 15.4076 |  |  |  |  | 0.84 | 14.6205 | 0.14621
11:23 | 4092 | 73 | 265.9 | 10.3 | 84 | 14.6205 | 0.68327 | 15.3767 |  |  |  |  | 0.85 | 14.7217 | 0.14671 |  | 0.2941
11:23 | 4093 | 73 | 265.9 | 10.3 | 85 | 14.6205 | 0.68327 | 15.3449 |  |  |  |  | 0.86 | 14.7231 | 0.14722
11:23 | 4093 | 74 | 266 | 10.3 | 86 | 14.7217 | 0.68315 | 15.3122 |  |  |  |  | 0.87 | 14.7258 | 0.14724 |  | 0.29452
11:23 | 4094 | 74 | 266.1 | 10.4 | 87 | 14.7231 | 0.68302 | 15.2787 |  |  |  |  | 0.88 | 14.7285 | 0.14727
11:23 | 4095 | 74 | 266.3 | 10.4 | 88 | 14.7258 | 0.68277 | 15.2442 |  |  |  |  | 0.89 | 14.5281 | 0.14628 |  | 0.29056
11:23 | 4094 | 74 | 266.5 | 10.4 | 89 | 14.7285 | 0.68251 | 15.209 |  |  |  |  | 0.9 | 14.3263 | 0.14427
11:23 | 4092 | 72 | 266.5 | 10.4 | 90 | 14.5281 | 0.68251 | 15.1728 |  |  |  |  | 0.91 | 13.5911 | 0.13959 |  | 0.27207
11:23 | 4092 | 70 | 266.6 | 10.3 | 91 | 14.3263 | 0.68239 | 15.1359 |  |  |  |  | 0.92 | 12.9301 | 0.13261
11:23 | 4101 | 63 | 266.6 | 10.3 | 92 | 13.5911 | 0.68239 | 15.0981 |  |  |  |  | 0.93 | 12.9301 | 0.1293 |  | 0.25898
11:23 | 4101 | 57 | 266.8 | 10.3 | 93 | 12.9301 | 0.68213 | 15.0595 |  |  |  |  | 0.94 | 13.043 | 0.12987
11:23 | 4103 | 57 | 266.8 | 10.4 | 94 | 12.9301 | 0.68213 | 15.02 |  |  |  |  | 0.95 | 13.155 | 0.13099 |  | 0.26663
11:23 | 4104 | 58 | 266.8 | 10.4 | 95 | 13.043 | 0.68213 | 14.9798 |  |  |  |  | 0.96 | 14.3263 | 0.13741
11:23 | 4099 | 59 | 266.8 | 10.3 | 96 | 13.155 | 0.68213 | 14.9387 |  |  |  |  | 0.97 | 14.3249 | 0.14326 |  | 0.28684
11:23 | 4095 | 70 | 266.6 | 10.3 | 97 | 14.3263 | 0.68239 | 14.8969 |  |  |  |  | 0.98 | 14.4256 | 0.14375
11:23 | 4093 | 70 | 266.5 | 10.3 | 98 | 14.3249 | 0.68251 | 14.8543 |  |  |  |  | 0.99 | 14.5201 | 0.14473 |  | 0.29009
11:23 | 4079 | 71 | 266.4 | 10.3 | 99 | 14.4256 | 0.68264 | 14.8109 |  |  |  |  | 1 | 14.5201 | 0.1452
11:23 | 4079 | 72 | 265.9 | 10.3 | 100 | 14.5201 | 0.68327 | 14.7667 |  |  |  |  | 0 | 14.5241 | -14.5221 |  | -14.3782
11:23 | 4074 | 72 | 265.9 | 10.3 | 101 | 14.5201 | 0.68327 | 14.7218 |  |  |  |  | 0.01 | 14.5241 | 0.14524
11:23 | 4074 | 72 | 266.2 | 10.3 | 102 | 14.5241 | 0.68289 | 14.6761 |  |  |  |  | 0.02 | 14.2209 | 0.14373 |  | 0.28509
11:23 | 4070 | 72 | 266.2 | 10.3 | 103 | 14.5241 | 0.68289 | 14.6297 |  |  |  |  | 0.03 | 14.1188 | 0.1417
11:23 | 4068 | 69 | 266.4 | 10.3 | 104 | 14.2209 | 0.68264 | 14.5826 |  |  |  |  | 0.04 | 13.6947 | 0.13907 |  | 0.2753
11:23 | 4078 | 68 | 266.5 | 10.3 | 105 | 14.1188 | 0.68251 | 14.5347 |  |  |  |  | 0.05 | 13.6934 | 0.13694
11:23 | 4088 | 64 | 266.3 | 10.3 | 106 | 13.6947 | 0.68277 | 14.4861 |  |  |  |  | 0.06 | 14.2183 | 0.13956 |  | 0.28397
11:23 | 4090 | 64 | 266.2 | 10.3 | 107 | 13.6934 | 0.68289 | 14.4368 |  |  |  |  | 0.07 | 14.6246 | 0.14421
11:23 | 4102 | 69 | 266.2 | 10.3 | 108 | 14.2183 | 0.68289 | 14.3868 |  |  |  |  | 0.08 | 15.0199 | 0.14822 |  | 0.30035
11:23 | 4102 | 73 | 266.2 | 10.3 | 109 | 14.6246 | 0.68289 | 14.336 |  |  |  |  | 0.09 | 15.4008 | 0.1521
11:23 | 4110 | 77 | 266.2 | 10.3 | 110 | 15.0199 | 0.68289 | 14.2846 |  |  |  |  | 0.1 | 15.4008 | 0.15401 |  | 0.30706
11:23 | 4110 | 81 | 265.9 | 10.3 | 111 | 15.4008 | 0.68327 | 14.2326 |  |  |  |  | 0.11 | 15.1144 | 0.15258
11:23 | 4108 | 81 | 265.9 | 10.3 | 112 | 15.4008 | 0.68327 | 14.1798 |  |  |  |  | 0.12 | 15.1172 | 0.15116 |  | 0.29614
11:23 | 4106 | 78 | 266 | 10.3 | 113 | 15.1144 | 0.68315 | 14.1264 |  |  |  |  | 0.13 | 13.2599 | 0.14189
11:23 | 4095 | 78 | 266.2 | 10.3 | 114 | 15.1172 | 0.68289 | 14.0723 |  |  |  |  | 0.14 | 13.2611 | 0.1326 |  | 0.26334
11:23 | 4083 | 60 | 266.3 | 10.3 | 115 | 13.2599 | 0.68277 | 14.0176 |  |  |  |  | 0.15 | 12.6977 | 0.12979
11:23 | 4084 | 60 | 266.4 | 10.3 | 116 | 13.2611 | 0.68264 | 13.9623 |  |  |  |  | 0.16 | 12.2318 | 0.12465 |  | 0.24619
11:23 | 4089 | 55 | 266.5 | 10.3 | 117 | 12.6977 | 0.68251 | 13.9063 |  |  |  |  | 0.17 | 12.2318 | 0.12232
11:23 | 4089 | 51 | 266.9 | 10.3 | 118 | 12.2318 | 0.68201 | 13.8497 |  |  |  |  | 0.18 | 12.2318 | 0.12232 |  | 0.24464
11:23 | 4106 | 51 | 266.9 | 10.3 | 119 | 12.2318 | 0.68201 | 13.7924 |  |  |  |  | 0.19 | 12.2318 | 0.12232
11:23 | 4106 | 51 | 266.9 | 10.3 | 120 | 12.2318 | 0.68201 | 13.7346 |  |  |  |  | 0.2 | 12.2329 | 0.12232 |  | 0.24466
11:23 | 4111 | 51 | 266.9 | 10.3 | 121 | 12.2318 | 0.68201 | 13.6762 |  |  |  |  | 0.21 | 12.234 | 0.12233
11:23 | 4115 | 51 | 267 | 10.3 | 122 | 12.2329 | 0.68188 | 13.6171 |  |  |  |  | 0.22 | 12.2329 | 0.12233 |  | 0.24466
11:23 | 4118 | 51 | 267.1 | 10.3 | 123 | 12.234 | 0.68176 | 13.5575 |  |  |  |  | 0.23 | 12.2318 | 0.12232
11:23 | 4122 | 51 | 267 | 10.3 | 124 | 12.2329 | 0.68188 | 13.4973 |  |  |  |  | 0.24 | 12.3511 | 0.12291 |  | 0.24742
11:23 | 4122 | 51 | 266.9 | 10.3 | 125 | 12.2318 | 0.68201 | 13.4366 |  |  |  |  | 0.25 | 12.5911 | 0.12471
11:23 | 4124 | 52 | 266.9 | 10.3 | 126 | 12.3511 | 0.68201 | 13.3753 |  |  |  |  | 0.26 | 12.8221 | 0.12707 |  | 0.25644
11:23 | 4124 | 54 | 267.3 | 10.3 | 127 | 12.5911 | 0.6815 | 13.3134 |  |  |  |  | 0.27 | 13.0515 | 0.12937
11:23 | 4126 | 56 | 267.3 | 10.3 | 128 | 12.8221 | 0.6815 | 13.251 |  |  |  |  | 0.28 | 13.0515 | 0.13051 |  | 0.25911
11:23 | 4126 | 58 | 267.5 | 10.3 | 129 | 13.0515 | 0.68125 | 13.188 |  |  |  |  | 0.29 | 12.4762 | 0.12764
11:23 | 4128 | 58 | 267.5 | 10.3 | 130 | 13.0515 | 0.68125 | 13.1245 |  |  |  |  | 0.3 | 12.4751 | 0.12476 |  | 0.25066
11:23 | 4128 | 53 | 267.5 | 10.3 | 131 | 12.4762 | 0.68125 | 13.0606 |  |  |  |  | 0.31 | 12.8209 | 0.12648
11:23 | 4130 | 53 | 267.4 | 10.3 | 132 | 12.4751 | 0.68138 | 12.996 |  |  |  |  | 0.32 | 12.8185 | 0.1282 |  | 0.25825
11:23 | 4131 | 56 | 267.2 | 10.3 | 133 | 12.8209 | 0.68163 | 12.931 |  |  |  |  | 0.33 | 13.3786 | 0.13099
11:23 | 4131 | 56 | 267 | 10.4 | 134 | 12.8185 | 0.68188 | 12.8655 |  |  |  |  | 0.34 | 13.9148 | 0.13647 |  | 0.27651
11:23 | 4133 | 61 | 267 | 10.4 | 135 | 13.3786 | 0.68188 | 12.7995 |  |  |  |  | 0.35 | 13.9148 | 0.13915
11:23 | 4133 | 66 | 266.9 | 10.4 | 136 | 13.9148 | 0.68201 | 12.7331 |  |  |  |  | 0.36 | 13.9161 | 0.13915 |  | 0.27832
11:23 | 4114 | 66 | 266.9 | 10.4 | 137 | 13.9148 | 0.68201 | 12.6661 |  |  |  |  | 0.37 | 13.9161 | 0.13916
11:23 | 4113 | 66 | 267 | 10.4 | 138 | 13.9161 | 0.68188 | 12.5987 |  |  |  |  | 0.38 | 13.8115 | 0.13864 |  | 0.27658
11:23 | 4100 | 66 | 267 | 10.4 | 139 | 13.9161 | 0.68188 | 12.5308 |  |  |  |  | 0.39 | 13.8128 | 0.13812
11:23 | 4090 | 65 | 267.1 | 10.4 | 140 | 13.8115 | 0.68176 | 12.4625 |  |  |  |  | 0.4 | 12.4739 | 0.13143 |  | 0.25394
11:23 | 4093 | 65 | 267.2 | 10.4 | 141 | 13.8128 | 0.68163 | 12.3938 |  |  |  |  | 0.41 | 12.4739 | 0.12474
11:23 | 4096 | 53 | 267.3 | 10.4 | 142 | 12.4739 | 0.6815 | 12.3246 |  |  |  |  | 0.42 | 12.4739 | 0.12474 |  | 0.24908
11:23 | 4096 | 53 | 267.3 | 10.4 | 143 | 12.4739 | 0.6815 | 12.255 |  |  |  |  | 0.43 | 12.3557 | 0.12415
11:23 | 4096 | 53 | 267.3 | 10.4 | 144 | 12.4739 | 0.6815 | 12.1849 |  |  |  |  | 0.44 | 12.2363 | 0.12296 |  | 0.24473
11:23 | 4096 | 52 | 267.3 | 10.4 | 145 | 12.3557 | 0.6815 | 12.1145 |  |  |  |  | 0.45 | 12.1169 | 0.12177
11:23 | 4085 | 51 | 267.3 | 10.4 | 146 | 12.2363 | 0.6815 | 12.0437 |  |  |  |  | 0.46 | 12.1169 | 0.12117 |  | 0.24393
11:23 | 4084 | 50 | 267.4 | 10.4 | 147 | 12.1169 | 0.68138 | 11.9724 |  |  |  |  | 0.47 | 12.5957 | 0.12356
11:23 | 4081 | 50 | 267.4 | 10.4 | 148 | 12.1169 | 0.68138 | 11.9008 |  |  |  |  | 0.48 | 12.598 | 0.12597 |  | 0.25195
11:23 | 4079 | 54 | 267.7 | 10.4 | 149 | 12.5957 | 0.681 | 11.8288 |  |  |  |  | 0.49 | 12.598 | 0.12598
11:23 | 4084 | 54 | 267.9 | 10.4 | 150 | 12.598 | 0.68075 | 11.7565 |  |  |  |  | 0.5 | 12.598 | 0.12598 |  | 0.25196
11:23 | 4090 | 54 | 267.9 | 10.4 | 151 | 12.598 | 0.68075 | 11.6838 |  |  |  |  | 0.51 | 12.598 | 0.12598
11:23 | 4091 | 54 | 267.9 | 10.4 | 152 | 12.598 | 0.68075 | 11.6107 |  |  |  |  | 0.52 | 12.6004 | 0.12599 |  | 0.25277
11:23 | 4107 | 54 | 267.9 | 10.4 | 153 | 12.598 | 0.68075 | 11.5373 |  |  |  |  | 0.53 | 12.8316 | 0.12716
11:23 | 4107 | 54 | 268.1 | 10.4 | 154 | 12.6004 | 0.6805 | 11.4636 |  |  |  |  | 0.54 | 13.172 | 0.13002 |  | 0.26231
11:23 | 4118 | 56 | 268.1 | 10.4 | 155 | 12.8316 | 0.6805 | 11.3895 |  |  |  |  | 0.55 | 13.172 | 0.13172
11:23 | 4120 | 59 | 268.2 | 10.4 | 156 | 13.172 | 0.68037 | 11.3151 |  |  |  |  | 0.56 | 13.3934 | 0.13283 |  | 0.26713
11:23 | 4116 | 59 | 268.2 | 10.3 | 157 | 13.172 | 0.68037 | 11.2404 |  |  |  |  | 0.57 | 13.3922 | 0.13393
11:23 | 4113 | 61 | 268.2 | 10.3 | 158 | 13.3934 | 0.68037 | 11.1654 |  |  |  |  | 0.58 | 13.2832 | 0.13338 |  | 0.26603
11:23 | 4112 | 61 | 268.1 | 10.4 | 159 | 13.3922 | 0.6805 | 11.0901 |  |  |  |  | 0.59 | 13.2832 | 0.13283
11:23 | 4111 | 60 | 268.2 | 10.4 | 160 | 13.2832 | 0.68037 | 11.0145 |  |  |  |  | 0.6 | 12.4843 | 0.12884 |  | 0.25034
11:23 | 4111 | 60 | 268.2 | 10.3 | 161 | 13.2832 | 0.68037 | 10.9386 |  |  |  |  | 0.61 | 11.8819 | 0.12183
11:23 | 4109 | 53 | 268.2 | 10.3 | 162 | 12.4843 | 0.68037 | 10.8624 |  |  |  |  | 0.62 | 11.5046 | 0.11693 |  | 0.22961
11:23 | 4109 | 48 | 268.3 | 10.3 | 163 | 11.8819 | 0.68024 | 10.786 |  |  |  |  | 0.63 | 10.9814 | 0.11243
11:23 | 4100 | 45 | 268.3 | 10.3 | 164 | 11.5046 | 0.68024 | 10.7094 |  |  |  |  | 0.64 | 10.9814 | 0.10981 |  | 0.22005
11:23 | 4099 | 41 | 268.3 | 10.3 | 165 | 10.9814 | 0.68024 | 10.6325 |  |  |  |  | 0.65 | 11.1084 | 0.11045
11:23 | 4100 | 41 | 268.3 | 10.3 | 166 | 10.9814 | 0.68024 | 10.5553 |  |  |  |  | 0.66 | 11.1032 | 0.11106 |  | 0.22338
11:23 | 4101 | 42 | 267.7 | 10.3 | 167 | 11.1084 | 0.681 | 10.4779 |  |  |  |  | 0.67 | 11.494 | 0.11299
11:23 | 4100 | 42 | 267.2 | 10.4 | 168 | 11.1032 | 0.68163 | 10.4003 |  |  |  |  | 0.68 | 11.6221 | 0.11558 |  | 0.22985
11:23 | 4098 | 45 | 267.3 | 10.4 | 169 | 11.494 | 0.6815 | 10.3225 |  |  |  |  | 0.69 | 10.9723 | 0.11297
11:23 | 4097 | 46 | 267.4 | 10.4 | 170 | 11.6221 | 0.68138 | 10.2444 |  |  |  |  | 0.7 | 10.5671 | 0.1077 |  | 0.21223
11:23 | 4089 | 41 | 267.4 | 10.4 | 171 | 10.9723 | 0.68138 | 10.1662 |  |  |  |  | 0.71 | 10.4272 | 0.10497
11:23 | 4089 | 38 | 267.8 | 10.4 | 172 | 10.5671 | 0.68087 | 10.0878 |  |  |  |  | 0.72 | 10.2872 | 0.10357 |  | 0.20573
11:23 | 4081 | 37 | 267.8 | 10.3 | 173 | 10.4272 | 0.68087 | 10.0092 |  |  |  |  | 0.73 | 10.1443 | 0.10216
11:23 | 4079 | 36 | 268 | 10.3 | 174 | 10.2872 | 0.68062 | 9.9304 |  |  |  |  | 0.74 | 9.2348 | 0.096895 |  | 0.18773
11:23 | 4082 | 35 | 268.1 | 10.3 | 175 | 10.1443 | 0.6805 | 9.8514 |  |  |  |  | 0.75 | 9.2356 | 0.092352
11:23 | 4084 | 29 | 268.2 | 10.3 | 176 | 9.2348 | 0.68037 | 9.7723 |  |  |  |  | 0.76 | 8.9114 | 0.090735 |  | 0.17875
11:23 | 4089 | 29 | 268.3 | 10.3 | 177 | 9.2356 | 0.68024 | 9.693 |  |  |  |  | 0.77 | 8.7449 | 0.088282
11:23 | 4096 | 27 | 268.3 | 10.3 | 178 | 8.9114 | 0.68024 | 9.6136 |  |  |  |  | 0.78 | 8.2249 | 0.084849 |  | 0.16502
11:23 | 4096 | 26 | 268.3 | 10.3 | 179 | 8.7449 | 0.68024 | 9.5341 |  |  |  |  | 0.79 | 7.8606 | 0.080428
11:23 | 4101 | 23 | 268.3 | 10.3 | 180 | 8.2249 | 0.68024 | 9.4544 |  |  |  |  | 0.8 | 7.4769 | 0.076688 |  | 0.14946
11:23 | 4101 | 21 | 268.5 | 10.3 | 181 | 7.8606 | 0.67999 | 9.3746 |  |  |  |  | 0.81 | 7.0712 | 0.07274
11:23 | 4097 | 19 | 268.5 | 10.4 | 182 | 7.4769 | 0.67999 | 9.2947 |  |  |  |  | 0.82 | 7.0705 | 0.070708 |  | 0.13998
11:23 | 4097 | 17 | 268.3 | 10.4 | 183 | 7.0712 | 0.68024 | 9.2147 |  |  |  |  | 0.83 | 6.6422 | 0.068564
11:23 | 4095 | 17 | 268.2 | 10.4 | 184 | 7.0705 | 0.68037 | 9.1346 |  |  |  |  | 0.84 | 6.6428 | 0.066425 |  | 0.13428
11:23 | 4094 | 15 | 268.3 | 10.4 | 185 | 6.6422 | 0.68024 | 9.0544 |  |  |  |  | 0.85 | 7.0712 | 0.06857
11:23 | 4090 | 15 | 268.4 | 10.4 | 186 | 6.6428 | 0.68012 | 8.9741 |  |  |  |  | 0.86 | 7.2748 | 0.07173 |  | 0.14548
11:23 | 4082 | 17 | 268.3 | 10.4 | 187 | 7.0712 | 0.68024 | 8.8937 |  |  |  |  | 0.87 | 7.4742 | 0.073745
11:23 | 4082 | 18 | 268.1 | 10.4 | 188 | 7.2748 | 0.6805 | 8.8133 |  |  |  |  | 0.88 | 7.669 | 0.075716 |  | 0.15458
11:23 | 4077 | 19 | 268.1 | 10.4 | 189 | 7.4742 | 0.6805 | 8.7329 |  |  |  |  | 0.89 | 8.2241 | 0.079466
11:23 | 4077 | 20 | 268.2 | 10.4 | 190 | 7.669 | 0.68037 | 8.6523 |  |  |  |  | 0.9 | 9.2322 | 0.087282 |  | 0.18128
11:23 | 4080 | 23 | 268.2 | 10.4 | 191 | 8.2241 | 0.68037 | 8.5718 |  |  |  |  | 0.91 | 9.2313 | 0.092318
11:23 | 4081 | 29 | 267.9 | 10.4 | 192 | 9.2322 | 0.68075 | 8.4912 |  |  |  |  | 0.92 | 9.9964 | 0.096139 |  | 0.19738
11:23 | 4088 | 29 | 267.8 | 10.4 | 193 | 9.2313 | 0.68087 | 8.4106 |  |  |  |  | 0.93 | 9.9974 | 0.099969
11:23 | 4095 | 34 | 267.9 | 10.4 | 194 | 9.9964 | 0.68075 | 8.3299 |  |  |  |  | 0.94 | 9.8502 | 0.099238 |  | 0.1975
11:23 | 4097 | 34 | 268 | 10.4 | 195 | 9.9974 | 0.68062 | 8.2493 |  |  |  |  | 0.95 | 9.8511 | 0.098506
11:23 | 4099 | 33 | 268.1 | 10.4 | 196 | 9.8502 | 0.6805 | 8.1687 |  |  |  |  | 0.96 | 9.2339 | 0.095425 |  | 0.18453
11:23 | 4099 | 33 | 268.2 | 10.3 | 197 | 9.8511 | 0.68037 | 8.088 |  |  |  |  | 0.97 | 8.5735 | 0.089037
11:23 | 4088 | 29 | 268.1 | 10.3 | 198 | 9.2339 | 0.6805 | 8.0074 |  |  |  |  | 0.98 | 8.4002 | 0.084869 |  | 0.16677
11:23 | 4088 | 25 | 268.1 | 10.3 | 199 | 8.5735 | 0.6805 | 7.9268 |  |  |  |  | 0.99 | 7.8577 | 0.08129
11:23 | 4078 | 24 | 268.1 | 10.3 | 200 | 8.4002 | 0.6805 | 7.8463 |  |  |  |  | 1 | 7.8577 | 0.078577
11:23 | 4075 | 21 | 268.1 | 10.3 | 201 | 7.8577 | 0.6805 | 7.7657
11:23 | 4076 | 21 | 268.1 | 10.3 | 202 | 7.8577 | 0.6805 | 7.6853
11:23 | 4077 | 19 | 268.1 | 10.3 | 203 | 7.4742 | 0.6805 | 7.6048
11:23 | 4083 | 19 | 268.2 | 10.3 | 204 | 7.4749 | 0.68037 | 7.5245
11:23 | 4092 | 16 | 268.1 | 10.3 | 205 | 6.8588 | 0.6805 | 7.4442
11:23 | 4093 | 15 | 267.7 | 10.3 | 206 | 6.6385 | 0.681 | 7.364
11:23 | 4096 | 14 | 267.7 | 10.3 | 207 | 6.4134 | 0.681 | 7.2839
11:23 | 4096 | 13 | 267.6 | 10.3 | 208 | 6.1796 | 0.68112 | 7.2039
11:23 | 4101 | 12 | 267.6 | 10.3 | 209 | 5.9371 | 0.68112 | 7.124
11:23 | 4102 | 11 | 267.4 | 10.3 | 210 | 5.6833 | 0.68138 | 7.0442
11:23 | 4107 | 11 | 267.3 | 10.3 |  | 5.6828 | 0.6815
11:23 | 4112 | 15 | 267.3 | 10.3 |  | 6.6361 | 0.6815
11:23 | 4116 | 15 | 267.3 | 10.3 |  | 6.6361 | 0.6815
11:23 | 4125 | 11 | 267.3 | 10.3 |  | 5.6828 | 0.6815
11:23 | 4125 | 10 | 267.3 | 10.3 |  | 5.4183 | 0.6815
11:23 | 4135 | 15 | 267.4 | 10.3 |  | 6.6367 | 0.68138
11:23 | 4135 | 18 | 267.6 | 10.3 |  | 7.2715 | 0.68112
11:23 | 4138 | 19 | 267.6 | 10.3 |  | 7.4707 | 0.68112
11:23 | 4140 | 22 | 267.5 | 10.3 |  | 8.0382 | 0.68125
11:23 | 4139 | 22 | 267.5 | 10.3 |  | 8.0382 | 0.68125
11:23 | 4138 | 22 | 267.5 | 10.3 |  | 8.0382 | 0.68125
11:23 | 4138 | 22 | 267.6 | 10.3 |  | 8.0389 | 0.68112
11:23 | 4138 | 19 | 267.7 | 10.3 |  | 7.4714 | 0.681
11:23 | 4138 | 18 | 267.8 | 10.3 |  | 7.2728 | 0.68087
11:23 | 4135 | 15 | 267.7 | 10.3 |  | 6.6385 | 0.681
11:23 | 4135 | 10 | 267.6 | 10.3 |  | 5.4198 | 0.68112
11:23 | 4136 | 10 | 267.6 | 10.3 |  | 5.4198 | 0.68112
11:23 | 4159 | 9 | 267.7 | 10.3 |  | 5.1422 | 0.681
11:23 | 4159 | 9 | 268 | 10.3 |  | 5.1436 | 0.68062
11:23 | 4164 | 9 | 268 | 10.3 |  | 5.1436 | 0.68062
11:23 | 4165 | 12 | 268 | 10.3 |  | 5.9393 | 0.68062
11:23 | 4161 | 12 | 267.9 | 10.3 |  | 5.9388 | 0.68075
11:23 | 4158 | 12 | 268.2 | 10.3 |  | 5.9404 | 0.68037
11:23 | 4154 | 12 | 268.3 | 10.3 |  | 5.941 | 0.68024
11:23 | 4144 | 10 | 268.4 | 10.3 |  | 5.4238 | 0.68012
11:24 | 4143 | 9 | 268.5 | 10.3 |  | 5.146 | 0.67999
11:24 | 4141 | 7 | 268.5 | 10.3 |  | 4.5383 | 0.67999
11:24 | 4141 | 6 | 268.2 | 10.3 |  | 4.2005 | 0.68037
11:24 | 4150 | 6 | 268.2 | 10.3 |  | 4.2005 | 0.68037
11:24 | 4154 | 7 | 268.2 | 10.3 |  | 4.5371 | 0.68037
11:24 | 4150 | 7 | 268.2 | 10.3 |  | 4.5371 | 0.68037
11:24 | 4146 | 10 | 268.2 | 10.3 |  | 5.4228 | 0.68037
11:24 | 4147 | 10 | 268.2 | 10.3 |  | 5.4228 | 0.68037
11:24 | 4148 | 7 | 268.2 | 10.3 |  | 4.5371 | 0.68037
11:24 | 4148 | 6 | 268.4 | 10.3 |  | 4.2013 | 0.68012
11:24 | 4141 | 7 | 268.4 | 10.3 |  | 4.5379 | 0.68012
11:24 | 4141 | 9 | 268.2 | 10.3 |  | 5.1446 | 0.68037
11:24 | 4133 | 9 | 268.2 | 10.3 |  | 5.1446 | 0.68037
11:24 | 4129 | 8 | 268.2 | 10.3 |  | 4.8503 | 0.68037
11:24 | 4130 | 8 | 268.2 | 10.3 |  | 4.8503 | 0.68037
11:24 | 4130 | 3 | 268.1 | 10.3 |  | 2.9699 | 0.6805
11:24 | 4128 | 3 | 268.1 | 10.3 |  | 2.9699 | 0.6805
11:24 | 4116 | 6 | 268.1 | 10.3 |  | 4.2001 | 0.6805
11:24 | 4116 | 7 | 268.2 | 10.3 |  | 4.5371 | 0.68037
11:24 | 4111 | 5 | 268.2 | 10.3 |  | 3.8345 | 0.68037
11:24 | 4111 | 4 | 268.1 | 10.3 |  | 3.4294 | 0.6805
11:24 | 4105 | 4 | 268.1 | 10.3 |  | 3.4294 | 0.6805
11:24 | 4101 | 6 | 268.2 | 10.3 |  | 4.2005 | 0.68037
11:24 | 4100 | 6 | 268.2 | 10.3 |  | 4.2005 | 0.68037
11:24 | 4099 | 8 | 268.3 | 10.3 |  | 4.8508 | 0.68024
11:24 | 4100 | 8 | 268.4 | 10.3 |  | 4.8512 | 0.68012
11:24 | 4107 | 10 | 268.3 | 10.3 |  | 5.4233 | 0.68024
11:24 | 4108 | 12 | 268.3 | 10.3 |  | 5.941 | 0.68024
11:24 | 4118 | 15 | 268.3 | 10.3 |  | 6.6422 | 0.68024
11:24 | 4118 | 17 | 267.9 | 10.3 |  | 7.0686 | 0.68075
11:24 | 4116 | 17 | 267.9 | 10.3 |  | 7.0686 | 0.68075
11:24 | 4116 | 18 | 267.7 | 10.3 |  | 7.2721 | 0.681
11:24 | 4121 | 18 | 267.5 | 10.4 |  | 7.2708 | 0.68125
11:24 | 4125 | 31 | 267.6 | 10.4 |  | 9.5426 | 0.68112
11:24 | 4125 | 31 | 267.7 | 10.4 |  | 9.5435 | 0.681
11:24 | 4120 | 34 | 267.7 | 10.4 |  | 9.9946 | 0.681
11:24 | 4120 | 37 | 268 | 10.4 |  | 10.4291 | 0.68062
11:24 | 4102 | 34 | 268 | 10.4 |  | 9.9974 | 0.68062
11:24 | 4102 | 32 | 267.8 | 10.4 |  | 9.6971 | 0.68087
11:24 | 4110 | 33 | 267.8 | 10.4 |  | 9.8474 | 0.68087
11:24 | 4116 | 37 | 267.8 | 10.4 |  | 10.4272 | 0.68087
11:24 | 4119 | 37 | 267.8 | 10.4 |  | 10.4272 | 0.68087
11:24 | 4121 | 33 | 268 | 10.4 |  | 9.8492 | 0.68062
11:24 | 4121 | 33 | 268.2 | 10.4 |  | 9.8511 | 0.68037
11:24 | 4120 | 33 | 268.2 | 10.4 |  | 9.8511 | 0.68037
11:24 | 4119 | 33 | 268.1 | 10.3 |  | 9.8502 | 0.6805
11:24 | 4104 | 32 | 268.1 | 10.3 |  | 9.6998 | 0.6805
11:24 | 4104 | 32 | 268 | 10.3 |  | 9.6989 | 0.68062
11:24 | 4104 | 32 | 268 | 10.3 |  | 9.6989 | 0.68062
11:24 | 4107 | 31 | 268 | 10.3 |  | 9.5461 | 0.68062
11:24 | 4109 | 27 | 267.9 | 10.3 |  | 8.9082 | 0.68075
11:24 | 4123 | 27 | 267.8 | 10.3 |  | 8.9073 | 0.68087
11:24 | 4137 | 28 | 267.6 | 10.3 |  | 9.0691 | 0.68112
11:24 | 4136 | 28 | 267.5 | 10.3 |  | 9.0683 | 0.68125
11:24 | 4124 | 29 | 267.5 | 10.3 |  | 9.2288 | 0.68125
11:24 | 4124 | 30 | 267.5 | 10.3 |  | 9.3866 | 0.68125
11:24 | 4109 | 32 | 267.5 | 10.4 |  | 9.6944 | 0.68125
11:24 | 4109 | 35 | 267.8 | 10.4 |  | 10.1414 | 0.68087
11:24 | 4109 | 35 | 267.8 | 10.4 |  | 10.1414 | 0.68087
11:24 | 4110 | 41 | 267.9 | 10.4 |  | 10.9774 | 0.68075
11:24 | 4102 | 41 | 268 | 10.4 |  | 10.9784 | 0.68062
11:24 | 4095 | 38 | 268 | 10.4 |  | 10.5691 | 0.68062
11:24 | 4095 | 38 | 268 | 10.3 |  | 10.5691 | 0.68062
11:24 | 4101 | 39 | 268 | 10.3 |  | 10.7073 | 0.68062
11:24 | 4101 | 39 | 267.8 | 10.3 |  | 10.7053 | 0.68087
11:24 | 4106 | 42 | 267.8 | 10.2 |  | 11.1094 | 0.68087
11:24 | 4106 | 45 | 267.3 | 10.2 |  | 11.494 | 0.6815
11:24 | 4101 | 45 | 267.3 | 10.2 |  | 11.494 | 0.6815
11:24 | 4097 | 51 | 267.3 | 10.2 |  | 12.2363 | 0.6815
11:24 | 4094 | 51 | 267.3 | 10.3 |  | 12.2363 | 0.6815
11:24 | 4091 | 55 | 267.4 | 10.3 |  | 12.7083 | 0.68138
11:24 | 4091 | 55 | 267.5 | 10.3 |  | 12.7094 | 0.68125
11:24 | 4080 | 57 | 267.5 | 10.3 |  | 12.9385 | 0.68125
11:24 | 4080 | 59 | 267.8 | 10.3 |  | 13.1672 | 0.68087
11:24 | 4077 | 54 | 267.8 | 10.3 |  | 12.5969 | 0.68087
11:24 | 4077 | 49 | 267.9 | 10.3 |  | 12.0006 | 0.68075
11:24 | 4084 | 49 | 267.9 | 10.3 |  | 12.0006 | 0.68075
11:24 | 4090 | 48 | 267.9 | 10.3 |  | 11.8775 | 0.68075
11:24 | 4092 | 48 | 267.8 | 10.3 |  | 11.8764 | 0.68087
11:24 | 4094 | 48 | 267.8 | 10.3 |  | 11.8764 | 0.68087
11:24 | 4093 | 48 | 267.8 | 10.3 |  | 11.8764 | 0.68087
11:24 | 4077 | 50 | 267.8 | 10.3 |  | 12.1213 | 0.68087
11:24 | 4077 | 51 | 267.6 | 10.3 |  | 12.2397 | 0.68112
11:24 | 4067 | 57 | 267.6 | 10.3 |  | 12.9397 | 0.68112
11:24 | 4066 | 65 | 267.6 | 10.3 |  | 13.8179 | 0.68112
11:24 | 4062 | 64 | 267.6 | 10.3 |  | 13.7112 | 0.68112
11:24 | 4059 | 56 | 267.7 | 10.3 |  | 12.8268 | 0.681
11:24 | 4065 | 56 | 267.9 | 10.3 |  | 12.8292 | 0.68075
11:24 | 4073 | 48 | 267.9 | 10.3 |  | 11.8775 | 0.68075
11:24 | 4074 | 48 | 267.9 | 10.3 |  | 11.8775 | 0.68075
11:24 | 4091 | 47 | 267.9 | 10.3 |  | 11.7532 | 0.68075
11:24 | 4091 | 47 | 268.1 | 10.3 |  | 11.7553 | 0.6805
11:24 | 4087 | 48 | 268.1 | 10.3 |  | 11.8797 | 0.6805
11:24 | 4087 | 49 | 268.1 | 10.3 |  | 12.0028 | 0.6805
11:24 | 4076 | 49 | 268.1 | 10.3 |  | 12.0028 | 0.6805
11:24 | 4066 | 45 | 267.9 | 10.3 |  | 11.5004 | 0.68075
11:24 | 4054 | 45 | 267.8 | 10.2 |  | 11.4993 | 0.68087
11:24 | 4039 | 46 | 267.7 | 10.2 |  | 11.6253 | 0.681
11:24 | 4038 | 46 | 267.6 | 10.2 |  | 11.6242 | 0.68112
11:24 | 4021 | 49 | 267.6 | 10.2 |  | 11.9973 | 0.68112
11:24 | 4021 | 51 | 267.3 | 10.2 |  | 12.2363 | 0.6815
11:24 | 4038 | 52 | 267.3 | 10.2 |  | 12.3557 | 0.6815
11:24 | 4041 | 54 | 267.4 | 10.2 |  | 12.5922 | 0.68138
11:24 | 4042 | 55 | 267.4 | 10.2 |  | 12.7083 | 0.68138
11:24 | 4043 | 63 | 267.4 | 10.2 |  | 13.6011 | 0.68138
11:24 | 4048 | 63 | 267.4 | 10.2 |  | 13.6011 | 0.68138
11:24 | 4054 | 57 | 267.3 | 10.2 |  | 12.9361 | 0.6815
11:24 | 4055 | 57 | 267.2 | 10.2 |  | 12.9349 | 0.68163
11:24 | 4068 | 61 | 267.3 | 10.2 |  | 13.3823 | 0.6815
11:24 | 4068 | 64 | 267.4 | 10.2 |  | 13.7087 | 0.68138
11:24 | 4070 | 63 | 267.4 | 10.2 |  | 13.6011 | 0.68138
11:24 | 4071 | 60 | 267.4 | 10.2 |  | 13.2734 | 0.68138
11:24 | 4083 | 60 | 267.4 | 10.2 |  | 13.2734 | 0.68138
11:24 | 4094 | 66 | 267.4 | 10.2 |  | 13.9212 | 0.68138
11:24 | 4098 | 66 | 267.4 | 10.2 |  | 13.9212 | 0.68138
11:24 | 4104 | 68 | 267.4 | 10.2 |  | 14.1306 | 0.68138
11:24 | 4104 | 68 | 267.4 | 10.3 |  | 14.1306 | 0.68138
11:24 | 4111 | 70 | 267.3 | 10.3 |  | 14.3355 | 0.6815
11:24 | 4111 | 71 | 266.8 | 10.3 |  | 14.4309 | 0.68213
11:24 | 4103 | 72 | 266.8 | 10.3 |  | 14.5322 | 0.68213
11:24 | 4102 | 73 | 267.1 | 10.3 |  | 14.6368 | 0.68176
11:24 | 4099 | 73 | 267.2 | 10.3 |  | 14.6382 | 0.68163
11:24 | 4096 | 75 | 267.4 | 10.3 |  | 14.8401 | 0.68138
11:24 | 4095 | 75 | 267.5 | 10.3 |  | 14.8414 | 0.68125
11:24 | 4093 | 68 | 267.4 | 10.3 |  | 14.1306 | 0.68138
11:24 | 4094 | 67 | 267.3 | 10.3 |  | 14.025 | 0.6815
11:24 | 4108 | 69 | 267.3 | 10.3 |  | 14.2328 | 0.6815
11:24 | 4108 | 71 | 267.1 | 10.3 |  | 14.4349 | 0.68176
11:24 | 4109 | 73 | 267.1 | 10.3 |  | 14.6368 | 0.68176
11:24 | 4109 | 76 | 266.9 | 10.3 |  | 14.9318 | 0.68201
11:24 | 4111 | 76 | 266.8 | 10.3 |  | 14.9304 | 0.68213
11:24 | 4113 | 78 | 266.9 | 10.3 |  | 15.127 | 0.68201
11:24 | 4112 | 78 | 266.9 | 10.3 |  | 15.127 | 0.68201
11:24 | 4110 | 78 | 266.9 | 10.3 |  | 15.127 | 0.68201
11:24 | 4109 | 78 | 267 | 10.3 |  | 15.1284 | 0.68188
11:24 | 4101 | 78 | 267 | 10.3 |  | 15.1284 | 0.68188
11:24 | 4101 | 78 | 266.6 | 10.3 |  | 15.1228 | 0.68239
11:24 | 4102 | 78 | 266.6 | 10.3 |  | 15.1228 | 0.68239
11:24 | 4102 | 78 | 266.6 | 10.3 |  | 15.1228 | 0.68239
11:24 | 4102 | 78 | 266.6 | 10.3 |  | 15.1228 | 0.68239
11:24 | 4103 | 78 | 266.7 | 10.3 |  | 15.1242 | 0.68226
11:24 | 4100 | 78 | 266.8 | 10.3 |  | 15.1256 | 0.68213
11:24 | 4095 | 84 | 266.8 | 10.3 |  | 15.6965 | 0.68213
11:24 | 4095 | 86 | 266.8 | 10.3 |  | 15.8823 | 0.68213
11:24 | 4101 | 85 | 266.8 | 10.3 |  | 15.7897 | 0.68213
11:24 | 4101 | 85 | 266.9 | 10.3 |  | 15.7912 | 0.68201
11:24 | 4106 | 83 | 266.9 | 10.3 |  | 15.6043 | 0.68201
11:24 | 4107 | 76 | 266.7 | 10.3 |  | 14.929 | 0.68226
11:24 | 4109 | 76 | 266.7 | 10.3 |  | 14.929 | 0.68226
11:24 | 4112 | 77 | 266.6 | 10.3 |  | 15.0255 | 0.68239
11:24 | 4114 | 77 | 266.6 | 10.3 |  | 15.0255 | 0.68239
11:24 | 4120 | 85 | 266.7 | 10.3 |  | 15.7882 | 0.68226
11:24 | 4120 | 87 | 267.2 | 10.3 |  | 15.9803 | 0.68163
11:24 | 4126 | 92 | 267.2 | 10.3 |  | 16.4331 | 0.68163
11:24 | 4126 | 95 | 266.9 | 10.3 |  | 16.6942 | 0.68201
11:24 | 4118 | 97 | 266.9 | 10.3 |  | 16.869 | 0.68201
11:24 | 4116 | 102 | 266.6 | 10.3 |  | 17.2935 | 0.68239
11:24 | 4113 | 102 | 266.5 | 10.4 |  | 17.2919 | 0.68251
11:24 | 4110 | 102 | 266.6 | 10.4 |  | 17.2935 | 0.68239
11:24 | 4106 | 102 | 266.7 | 10.4 |  | 17.2951 | 0.68226
11:24 | 4097 | 96 | 266.8 | 10.4 |  | 16.7803 | 0.68213
11:24 | 4097 | 94 | 267.1 | 10.4 |  | 16.6092 | 0.68176
11:24 | 4097 | 91 | 267.1 | 10.4 |  | 16.342 | 0.68176
11:24 | 4097 | 89 | 267.4 | 10.4 |  | 16.1659 | 0.68138
11:24 | 4097 | 89 | 267.4 | 10.4 |  | 16.1659 | 0.68138
11:24 | 4098 | 91 | 267.3 | 10.4 |  | 16.345 | 0.6815
11:24 | 4090 | 91 | 267.2 | 10.4 |  | 16.3435 | 0.68163
11:24 | 4083 | 94 | 267.1 | 10.4 |  | 16.6092 | 0.68176
11:24 | 4081 | 94 | 267.1 | 10.4 |  | 16.6092 | 0.68176
11:24 | 4076 | 92 | 267.1 | 10.4 |  | 16.4316 | 0.68176
11:24 | 4076 | 92 | 267 | 10.4 |  | 16.43 | 0.68188
11:24 | 4078 | 91 | 267 | 10.3 |  | 16.3405 | 0.68188
11:24 | 4078 | 91 | 267.3 | 10.3 |  | 16.345 | 0.6815
11:24 | 4083 | 91 | 267.3 | 10.3 |  | 16.345 | 0.6815
11:24 | 4085 | 90 | 267.5 | 10.3 |  | 16.258 | 0.68125
11:24 | 4092 | 90 | 267.6 | 10.3 |  | 16.2595 | 0.68112
11:24 | 4098 | 89 | 267.7 | 10.3 |  | 16.1704 | 0.681
11:24 | 4100 | 89 | 267.8 | 10.3 |  | 16.1719 | 0.68087
11:24 | 4105 | 91 | 267.8 | 10.3 |  | 16.3526 | 0.68087
11:24 | 4104 | 93 | 267.7 | 10.3 |  | 16.5298 | 0.681
11:24 | 4096 | 94 | 267.6 | 10.3 |  | 16.6169 | 0.68112
11:24 | 4096 | 95 | 266.8 | 10.3 |  | 16.6927 | 0.68213
11:24 | 4082 | 95 | 266.8 | 10.4 |  | 16.6927 | 0.68213
11:24 | 4075 | 94 | 266.7 | 10.4 |  | 16.603 | 0.68226
11:24 | 4075 | 94 | 266.6 | 10.4 |  | 16.6015 | 0.68239
11:24 | 4076 | 92 | 266.7 | 10.4 |  | 16.4255 | 0.68226
11:24 | 4078 | 92 | 266.8 | 10.4 |  | 16.427 | 0.68213
11:24 | 4087 | 92 | 266.7 | 10.4 |  | 16.4255 | 0.68226
11:24 | 4088 | 92 | 266.2 | 10.4 |  | 16.4179 | 0.68289
11:24 | 4107 | 90 | 266.2 | 10.4 |  | 16.2384 | 0.68289
11:24 | 4107 | 88 | 266.1 | 10.4 |  | 16.0555 | 0.68302
11:24 | 4110 | 88 | 266.1 | 10.4 |  | 16.0555 | 0.68302
11:24 | 4112 | 90 | 266.2 | 10.4 |  | 16.2384 | 0.68289
11:24 | 4105 | 90 | 266.2 | 10.3 |  | 16.2384 | 0.68289
11:24 | 4099 | 86 | 266.3 | 10.3 |  | 15.8749 | 0.68277
11:24 | 4098 | 86 | 266.4 | 10.3 |  | 15.8764 | 0.68264
11:24 | 4095 | 82 | 266.4 | 10.3 |  | 15.5028 | 0.68264
11:24 | 4095 | 81 | 266.5 | 10.3 |  | 15.4094 | 0.68251
11:24 | 4096 | 77 | 266.5 | 10.3 |  | 15.0241 | 0.68251
11:24 | 4096 | 74 | 266.2 | 10.3 |  | 14.7244 | 0.68289

## P4
| Port | 4
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current
| Pa | Pa | Deg C | mA
Averages | 4108.7321 | 42.5473 | 263.5804 | 10.3485 | [11 empty] | 12.5071 |  | 12.6069
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current |  |  |  |  | a | b | n | h | xi | f(xi) | Aj
| Pa. | Pa | Deg C | mA |  | 11.3232 |  |  | 0 | 1 | 100 | 0.01 | 0 | 13.6439
[6 empty] | vel | dens | [5 empty] | 0.01 | 13.6439 | 0.13644 |  | 0.27252
11:26 | 4155 | 64 | 262.3 | 10.4 | 1 | 13.6439 | 0.68786 | 15.2831 |  |  |  |  | 0.02 | 13.5368 | 0.1359
11:26 | 4145 | 64 | 262.3 | 10.4 | 2 | 13.6439 | 0.68786 | 15.2731 |  |  |  |  | 0.03 | 13.5368 | 0.13537 |  | 0.27073
11:26 | 4145 | 63 | 262.3 | 10.4 | 3 | 13.5368 | 0.68786 | 15.2631 |  |  |  |  | 0.04 | 13.5356 | 0.13536
11:26 | 4147 | 63 | 262.3 | 10.4 | 4 | 13.5368 | 0.68786 | 15.2529 |  |  |  |  | 0.05 | 13.5343 | 0.13535 |  | 0.2714
11:26 | 4149 | 63 | 262.2 | 10.4 | 5 | 13.5356 | 0.68799 | 15.2428 |  |  |  |  | 0.06 | 13.7475 | 0.13641
11:26 | 4151 | 63 | 262.1 | 10.4 | 6 | 13.5343 | 0.68812 | 15.2325 |  |  |  |  | 0.07 | 13.8515 | 0.138 |  | 0.27772
11:26 | 4154 | 65 | 262.1 | 10.4 | 7 | 13.7475 | 0.68812 | 15.2221 |  |  |  |  | 0.08 | 14.1628 | 0.14007
11:26 | 4154 | 66 | 262 | 10.3 | 8 | 13.8515 | 0.68825 | 15.2117 |  |  |  |  | 0.09 | 14.4634 | 0.14313 |  | 0.28827
11:26 | 4155 | 69 | 262 | 10.3 | 9 | 14.1628 | 0.68825 | 15.2011 |  |  |  |  | 0.1 | 14.4634 | 0.14463
11:26 | 4155 | 72 | 261.7 | 10.3 | 10 | 14.4634 | 0.68864 | 15.1905 |  |  |  |  | 0.11 | 14.3653 | 0.14414 |  | 0.28764
11:26 | 4166 | 72 | 261.7 | 10.3 | 11 | 14.4634 | 0.68864 | 15.1797 |  |  |  |  | 0.12 | 14.3666 | 0.14366
11:26 | 4172 | 71 | 261.9 | 10.3 | 12 | 14.3653 | 0.68838 | 15.1688 |  |  |  |  | 0.13 | 15.2515 | 0.14809 |  | 0.30208
11:26 | 4170 | 71 | 262 | 10.3 | 13 | 14.3666 | 0.68825 | 15.1577 |  |  |  |  | 0.14 | 15.2515 | 0.15251
11:26 | 4168 | 80 | 262.1 | 10.3 | 14 | 15.2515 | 0.68812 | 15.1465 |  |  |  |  | 0.15 | 15.7208 | 0.15486 |  | 0.31345
11:26 | 4169 | 80 | 262.1 | 10.3 | 15 | 15.2515 | 0.68812 | 15.1352 |  |  |  |  | 0.16 | 15.9003 | 0.15811
11:26 | 4171 | 85 | 262.1 | 10.3 | 16 | 15.7208 | 0.68812 | 15.1237 |  |  |  |  | 0.17 | 16.082 | 0.15991 |  | 0.32134
11:26 | 4171 | 87 | 261.8 | 10.3 | 17 | 15.9003 | 0.68851 | 15.1121 |  |  |  |  | 0.18 | 16.1751 | 0.16129
11:26 | 4162 | 89 | 261.8 | 10.3 | 18 | 16.082 | 0.68851 | 15.1003 |  |  |  |  | 0.19 | 16.1751 | 0.16175 |  | 0.3241
11:26 | 4162 | 90 | 262 | 10.3 | 19 | 16.1751 | 0.68825 | 15.0883 |  |  |  |  | 0.2 | 16.3538 | 0.16264
11:26 | 4152 | 90 | 262 | 10.3 | 20 | 16.1751 | 0.68825 | 15.0761 |  |  |  |  | 0.21 | 16.3554 | 0.16355 |  | 0.3256
11:26 | 4146 | 92 | 262 | 10.3 | 21 | 16.3538 | 0.68825 | 15.0638 |  |  |  |  | 0.22 | 15.9047 | 0.1613
11:26 | 4152 | 92 | 262.1 | 10.3 | 22 | 16.3554 | 0.68812 | 15.0512 |  |  |  |  | 0.23 | 15.9047 | 0.15905 |  | 0.31809
11:26 | 4157 | 87 | 262.1 | 10.3 | 23 | 15.9047 | 0.68812 | 15.0385 |  |  |  |  | 0.24 | 15.9047 | 0.15905
11:26 | 4158 | 87 | 262.1 | 10.3 | 24 | 15.9047 | 0.68812 | 15.0255 |  |  |  |  | 0.25 | 15.9062 | 0.15905 |  | 0.31843
11:26 | 4164 | 87 | 262.1 | 10.3 | 25 | 15.9047 | 0.68812 | 15.0123 |  |  |  |  | 0.26 | 15.9988 | 0.15953
11:26 | 4164 | 87 | 262.2 | 10.3 | 26 | 15.9062 | 0.68799 | 14.9989 |  |  |  |  | 0.27 | 16.094 | 0.16046 |  | 0.32186
11:26 | 4169 | 88 | 262.3 | 10.3 | 27 | 15.9988 | 0.68786 | 14.9853 |  |  |  |  | 0.28 | 16.1842 | 0.16139
11:26 | 4169 | 89 | 262.6 | 10.3 | 28 | 16.094 | 0.68748 | 14.9714 |  |  |  |  | 0.29 | 16.9725 | 0.16578 |  | 0.33682
11:26 | 4162 | 90 | 262.6 | 10.3 | 29 | 16.1842 | 0.68748 | 14.9573 |  |  |  |  | 0.3 | 16.9709 | 0.16972
11:26 | 4158 | 99 | 262.5 | 10.3 | 30 | 16.9725 | 0.68761 | 14.9429 |  |  |  |  | 0.31 | 16.0925 | 0.16532 |  | 0.32478
11:26 | 4150 | 99 | 262.4 | 10.3 | 31 | 16.9709 | 0.68774 | 14.9283 |  |  |  |  | 0.32 | 16.094 | 0.16093
11:26 | 4143 | 89 | 262.5 | 10.3 | 32 | 16.0925 | 0.68761 | 14.9134 |  |  |  |  | 0.33 | 15.6354 | 0.15865 |  | 0.31298
11:26 | 4142 | 89 | 262.6 | 10.3 | 33 | 16.094 | 0.68748 | 14.8982 |  |  |  |  | 0.34 | 15.2586 | 0.15447
11:26 | 4136 | 84 | 262.6 | 10.3 | 34 | 15.6354 | 0.68748 | 14.8828 |  |  |  |  | 0.35 | 15.0666 | 0.15163 |  | 0.30133
11:26 | 4136 | 80 | 262.6 | 10.3 | 35 | 15.2586 | 0.68748 | 14.8671 |  |  |  |  | 0.36 | 14.875 | 0.14971
11:26 | 4145 | 78 | 262.6 | 10.3 | 36 | 15.0666 | 0.68748 | 14.851 |  |  |  |  | 0.37 | 14.875 | 0.14875 |  | 0.29617
11:26 | 4145 | 76 | 262.8 | 10.3 | 37 | 14.875 | 0.68722 | 14.8347 |  |  |  |  | 0.38 | 14.4769 | 0.14676
11:26 | 4143 | 76 | 262.8 | 10.3 | 38 | 14.875 | 0.68722 | 14.818 |  |  |  |  | 0.39 | 14.4769 | 0.14477 |  | 0.29086
11:26 | 4141 | 72 | 262.7 | 10.3 | 39 | 14.4769 | 0.68735 | 14.8011 |  |  |  |  | 0.4 | 14.8722 | 0.14675
11:26 | 4137 | 72 | 262.7 | 10.3 | 40 | 14.4769 | 0.68735 | 14.7838 |  |  |  |  | 0.41 | 14.8708 | 0.14872 |  | 0.29965
11:26 | 4133 | 76 | 262.6 | 10.3 | 41 | 14.8722 | 0.68748 | 14.7662 |  |  |  |  | 0.42 | 15.5406 | 0.15206
11:26 | 4131 | 76 | 262.5 | 10.3 | 42 | 14.8708 | 0.68761 | 14.7482 |  |  |  |  | 0.43 | 15.9121 | 0.15726 |  | 0.31608
11:26 | 4116 | 83 | 262.5 | 10.3 | 43 | 15.5406 | 0.68761 | 14.7299 |  |  |  |  | 0.44 | 15.6354 | 0.15774
11:26 | 4116 | 87 | 262.6 | 10.3 | 44 | 15.9121 | 0.68748 | 14.7113 |  |  |  |  | 0.45 | 15.4467 | 0.15541 |  | 0.30956
11:26 | 4100 | 84 | 262.6 | 10.3 | 45 | 15.6354 | 0.68748 | 14.6923 |  |  |  |  | 0.46 | 15.4467 | 0.15447
11:26 | 4100 | 82 | 262.5 | 10.3 | 46 | 15.4467 | 0.68761 | 14.6729 |  |  |  |  | 0.47 | 15.4424 | 0.15445 |  | 0.30885
11:26 | 4097 | 82 | 262.5 | 10.3 | 47 | 15.4467 | 0.68761 | 14.6531 |  |  |  |  | 0.48 | 15.4395 | 0.15441
11:26 | 4095 | 82 | 262.2 | 10.3 | 48 | 15.4424 | 0.68799 | 14.633 |  |  |  |  | 0.49 | 15.2515 | 0.15345 |  | 0.30566
11:26 | 4098 | 82 | 262 | 10.3 | 49 | 15.4395 | 0.68825 | 14.6125 |  |  |  |  | 0.5 | 15.2529 | 0.15252
11:26 | 4102 | 80 | 262.1 | 10.3 | 50 | 15.2515 | 0.68812 | 14.5916 |  |  |  |  | 0.51 | 15.5362 | 0.15395 |  | 0.3104
11:26 | 4101 | 80 | 262.2 | 10.3 | 51 | 15.2529 | 0.68799 | 14.5703 |  |  |  |  | 0.52 | 15.7223 | 0.15629
11:26 | 4094 | 83 | 262.2 | 10.3 | 52 | 15.5362 | 0.68799 | 14.5485 |  |  |  |  | 0.53 | 15.5362 | 0.15629 |  | 0.31105
11:26 | 4094 | 85 | 262.2 | 10.3 | 53 | 15.7223 | 0.68799 | 14.5264 |  |  |  |  | 0.54 | 15.4481 | 0.15492
11:26 | 4085 | 83 | 262.2 | 10.3 | 54 | 15.5362 | 0.68799 | 14.5038 |  |  |  |  | 0.55 | 15.4481 | 0.15448 |  | 0.30928
11:26 | 4085 | 82 | 262.6 | 10.3 | 55 | 15.4481 | 0.68748 | 14.4809 |  |  |  |  | 0.56 | 15.5435 | 0.15496
11:26 | 4086 | 82 | 262.6 | 10.3 | 56 | 15.4481 | 0.68748 | 14.4574 |  |  |  |  | 0.57 | 15.5449 | 0.15544 |  | 0.30666
11:26 | 4087 | 83 | 262.7 | 10.3 | 57 | 15.5435 | 0.68735 | 14.4336 |  |  |  |  | 0.58 | 14.2758 | 0.1491
11:26 | 4089 | 83 | 262.8 | 10.3 | 58 | 15.5449 | 0.68722 | 14.4092 |  |  |  |  | 0.59 | 14.2758 | 0.14276 |  | 0.28449
11:26 | 4092 | 70 | 262.8 | 10.3 | 59 | 14.2758 | 0.68722 | 14.3845 |  |  |  |  | 0.6 | 13.9678 | 0.14122
11:26 | 4093 | 70 | 262.8 | 10.3 | 60 | 14.2758 | 0.68722 | 14.3592 |  |  |  |  | 0.61 | 13.7629 | 0.13865 |  | 0.27699
11:26 | 4110 | 67 | 262.9 | 10.3 | 61 | 13.9678 | 0.6871 | 14.3335 |  |  |  |  | 0.62 | 14.0769 | 0.1392
11:26 | 4110 | 65 | 263.3 | 10.3 | 62 | 13.7629 | 0.68658 | 14.3073 |  |  |  |  | 0.63 | 14.3867 | 0.14232 |  | 0.2867
11:26 | 4115 | 68 | 263.3 | 10.3 | 63 | 14.0769 | 0.68658 | 14.2806 |  |  |  |  | 0.64 | 14.3867 | 0.14387
11:26 | 4115 | 71 | 263.5 | 10.3 | 64 | 14.3867 | 0.68633 | 14.2534 |  |  |  |  | 0.65 | 14.6862 | 0.14536 |  | 0.29272
11:26 | 4120 | 71 | 263.5 | 10.3 | 65 | 14.3867 | 0.68633 | 14.2258 |  |  |  |  | 0.66 | 14.6848 | 0.14685
11:26 | 4124 | 74 | 263.4 | 10.3 | 66 | 14.6862 | 0.68646 | 14.1976 |  |  |  |  | 0.67 | 13.8683 | 0.14277 |  | 0.27973
11:26 | 4124 | 74 | 263.3 | 10.3 | 67 | 14.6848 | 0.68658 | 14.1689 |  |  |  |  | 0.68 | 13.7616 | 0.13815
11:26 | 4124 | 66 | 263.3 | 10.3 | 68 | 13.8683 | 0.68658 | 14.1396 |  |  |  |  | 0.69 | 13.7629 | 0.13762 |  | 0.2749
11:26 | 4124 | 65 | 263.2 | 10.3 | 69 | 13.7616 | 0.68671 | 14.1099 |  |  |  |  | 0.7 | 13.6579 | 0.1371
11:26 | 4129 | 65 | 263.3 | 10.3 | 70 | 13.7629 | 0.68658 | 14.0796 |  |  |  |  | 0.71 | 13.5507 | 0.13604 |  | 0.27064
11:26 | 4129 | 64 | 263.4 | 10.3 | 71 | 13.6579 | 0.68646 | 14.0488 |  |  |  |  | 0.72 | 13.3302 | 0.1344
11:26 | 4138 | 63 | 263.4 | 10.3 | 72 | 13.5507 | 0.68646 | 14.0174 |  |  |  |  | 0.73 | 13.439 | 0.13385 |  | 0.27189
11:26 | 4138 | 61 | 263.1 | 10.3 | 73 | 13.3302 | 0.68684 | 13.9855 |  |  |  |  | 0.74 | 14.481 | 0.1396
11:26 | 4141 | 62 | 263.1 | 10.3 | 74 | 13.439 | 0.68684 | 13.9529 |  |  |  |  | 0.75 | 14.4796 | 0.1448 |  | 0.29091
11:26 | 4143 | 72 | 263 | 10.3 | 75 | 14.481 | 0.68697 | 13.9199 |  |  |  |  | 0.76 | 14.875 | 0.14677
11:26 | 4141 | 72 | 262.9 | 10.3 | 76 | 14.4796 | 0.6871 | 13.8862 |  |  |  |  | 0.77 | 14.875 | 0.14875 |  | 0.29684
11:26 | 4139 | 76 | 262.8 | 10.3 | 77 | 14.875 | 0.68722 | 13.852 |  |  |  |  | 0.78 | 14.678 | 0.14776
11:26 | 4139 | 76 | 262.8 | 10.3 | 78 | 14.875 | 0.68722 | 13.8171 |  |  |  |  | 0.79 | 14.481 | 0.14579 |  | 0.28822
11:26 | 4129 | 74 | 262.8 | 10.3 | 79 | 14.678 | 0.68722 | 13.7817 |  |  |  |  | 0.8 | 13.8645 | 0.14173
11:26 | 4129 | 72 | 263 | 10.3 | 80 | 14.481 | 0.68697 | 13.7457 |  |  |  |  | 0.81 | 13.1074 | 0.13486 |  | 0.26467
11:26 | 4133 | 66 | 263 | 10.4 | 81 | 13.8645 | 0.68697 | 13.709 |  |  |  |  | 0.82 | 13.1074 | 0.13107
11:26 | 4133 | 59 | 262.9 | 10.4 | 82 | 13.1074 | 0.6871 | 13.6717 |  |  |  |  | 0.83 | 12.0686 | 0.12588 |  | 0.24484
11:26 | 4141 | 59 | 262.9 | 10.4 | 83 | 13.1074 | 0.6871 | 13.6338 |  |  |  |  | 0.84 | 12.0697 | 0.12069
11:26 | 4148 | 50 | 263.1 | 10.4 | 84 | 12.0686 | 0.68684 | 13.5953 |  |  |  |  | 0.85 | 11.827 | 0.11948 |  | 0.23735
11:26 | 4154 | 50 | 263.2 | 10.4 | 85 | 12.0697 | 0.68671 | 13.5561 |  |  |  |  | 0.86 | 11.8281 | 0.11828
11:26 | 4160 | 48 | 263.3 | 10.4 | 86 | 11.827 | 0.68658 | 13.5163 |  |  |  |  | 0.87 | 11.7042 | 0.11766 |  | 0.23408
11:26 | 4160 | 48 | 263.4 | 10.4 | 87 | 11.8281 | 0.68646 | 13.4758 |  |  |  |  | 0.88 | 11.5801 | 0.11642
11:26 | 4159 | 47 | 263.4 | 10.4 | 88 | 11.7042 | 0.68646 | 13.4346 |  |  |  |  | 0.89 | 11.8292 | 0.11705 |  | 0.23737
11:26 | 4159 | 46 | 263.5 | 10.4 | 89 | 11.5801 | 0.68633 | 13.3928 |  |  |  |  | 0.9 | 12.3133 | 0.12071
11:26 | 4155 | 48 | 263.5 | 10.4 | 90 | 11.8292 | 0.68633 | 13.3503 |  |  |  |  | 0.91 | 12.3133 | 0.12313 |  | 0.24705
11:26 | 4155 | 52 | 263.6 | 10.4 | 91 | 12.3133 | 0.6862 | 13.3071 |  |  |  |  | 0.92 | 12.5479 | 0.12431
11:26 | 4146 | 52 | 263.6 | 10.4 | 92 | 12.3133 | 0.6862 | 13.2632 |  |  |  |  | 0.93 | 12.5491 | 0.12548 |  | 0.24899
11:26 | 4139 | 54 | 263.6 | 10.4 | 93 | 12.5479 | 0.6862 | 13.2187 |  |  |  |  | 0.94 | 11.954 | 0.12252
11:26 | 4134 | 54 | 263.7 | 10.4 | 94 | 12.5491 | 0.68607 | 13.1734 |  |  |  |  | 0.95 | 11.954 | 0.11954 |  | 0.23742
11:26 | 4129 | 49 | 263.7 | 10.4 | 95 | 11.954 | 0.68607 | 13.1274 |  |  |  |  | 0.96 | 11.4557 | 0.11705
11:26 | 4129 | 49 | 263.7 | 10.4 | 96 | 11.954 | 0.68607 | 13.0807 |  |  |  |  | 0.97 | 10.9367 | 0.11196 |  | 0.22046
11:26 | 4136 | 45 | 263.7 | 10.4 | 97 | 11.4557 | 0.68607 | 13.0332 |  |  |  |  | 0.98 | 10.9367 | 0.10937
11:26 | 4136 | 41 | 263.9 | 10.4 | 98 | 10.9367 | 0.68582 | 12.985 |  |  |  |  | 0.99 | 10.8035 | 0.1087 |  | 0.21606
11:26 | 4125 | 41 | 263.9 | 10.4 | 99 | 10.9367 | 0.68582 | 12.9361 |  |  |  |  | 1 | 10.6676 | 0.10736
11:26 | 4123 | 40 | 264 | 10.4 | 100 | 10.8035 | 0.68569 | 12.8864 |  |  |  |  | 0 | 10.3886 | -10.5281 |  | -10.3304
11:26 | 4113 | 39 | 264 | 10.4 | 101 | 10.6676 | 0.68569 | 12.836 |  |  |  |  | 0.01 | 10.3866 | 0.10388
11:26 | 4104 | 37 | 263.8 | 10.4 | 102 | 10.3886 | 0.68594 | 12.7848 |  |  |  |  | 0.02 | 11.0662 | 0.10726 |  | 0.21906
11:26 | 4101 | 37 | 263.6 | 10.4 | 103 | 10.3866 | 0.6862 | 12.7329 |  |  |  |  | 0.03 | 11.0662 | 0.11066
11:26 | 4098 | 42 | 263.6 | 10.4 | 104 | 11.0662 | 0.6862 | 12.6801 |  |  |  |  | 0.04 | 11.4546 | 0.1126 |  | 0.22823
11:26 | 4098 | 42 | 263.6 | 10.4 | 105 | 11.0662 | 0.6862 | 12.6266 |  |  |  |  | 0.05 | 11.5833 | 0.11519
11:26 | 4102 | 45 | 263.6 | 10.4 | 106 | 11.4546 | 0.6862 | 12.5723 |  |  |  |  | 0.06 | 11.5833 | 0.11583 |  | 0.23167
11:26 | 4102 | 46 | 263.8 | 10.4 | 107 | 11.5833 | 0.68594 | 12.5172 |  |  |  |  | 0.07 | 11.5855 | 0.11584
11:26 | 4117 | 46 | 263.8 | 10.4 | 108 | 11.5833 | 0.68594 | 12.4612 |  |  |  |  | 0.08 | 11.5855 | 0.11585 |  | 0.23086
11:26 | 4120 | 46 | 264 | 10.4 | 109 | 11.5855 | 0.68569 | 12.4045 |  |  |  |  | 0.09 | 11.3308 | 0.11458
11:26 | 4116 | 46 | 264 | 10.4 | 110 | 11.5855 | 0.68569 | 12.347 |  |  |  |  | 0.1 | 11.3298 | 0.1133 |  | 0.22868
11:26 | 4111 | 44 | 264 | 10.4 | 111 | 11.3308 | 0.68569 | 12.2886 |  |  |  |  | 0.11 | 11.9551 | 0.11642
11:26 | 4114 | 44 | 263.9 | 10.4 | 112 | 11.3298 | 0.68582 | 12.2294 |  |  |  |  | 0.12 | 12.0753 | 0.12015 |  | 0.2407
11:26 | 4119 | 49 | 263.8 | 10.4 | 113 | 11.9551 | 0.68594 | 12.1693 |  |  |  |  | 0.13 | 11.954 | 0.12015
11:26 | 4119 | 50 | 263.7 | 10.4 | 114 | 12.0753 | 0.68607 | 12.1084 |  |  |  |  | 0.14 | 11.8303 | 0.11892 |  | 0.2366
11:26 | 4121 | 49 | 263.7 | 10.4 | 115 | 11.954 | 0.68607 | 12.0467 |  |  |  |  | 0.15 | 11.7064 | 0.11768
11:26 | 4121 | 48 | 263.6 | 10.4 | 116 | 11.8303 | 0.6862 | 11.984 |  |  |  |  | 0.16 | 11.3266 | 0.11516 |  | 0.2278
11:26 | 4119 | 47 | 263.6 | 10.4 | 117 | 11.7064 | 0.6862 | 11.9205 |  |  |  |  | 0.17 | 11.3266 | 0.11327
11:26 | 4119 | 44 | 263.6 | 10.4 | 118 | 11.3266 | 0.6862 | 11.8562 |  |  |  |  | 0.18 | 11.0672 | 0.11197 |  | 0.22221
11:26 | 4116 | 44 | 263.6 | 10.4 | 119 | 11.3266 | 0.6862 | 11.7909 |  |  |  |  | 0.19 | 11.0672 | 0.11067
11:26 | 4112 | 42 | 263.7 | 10.4 | 120 | 11.0672 | 0.68607 | 11.7248 |  |  |  |  | 0.2 | 10.8005 | 0.10934 |  | 0.2169
11:26 | 4114 | 42 | 263.7 | 10.4 | 121 | 11.0672 | 0.68607 | 11.6578 |  |  |  |  | 0.21 | 10.8015 | 0.10801
11:26 | 4117 | 40 | 263.7 | 10.4 | 122 | 10.8005 | 0.68607 | 11.5898 |  |  |  |  | 0.22 | 10.8015 | 0.10802 |  | 0.21603
11:26 | 4117 | 40 | 263.8 | 10.4 | 123 | 10.8015 | 0.68594 | 11.521 |  |  |  |  | 0.23 | 10.8025 | 0.10802
11:26 | 4124 | 40 | 263.8 | 10.4 | 124 | 10.8015 | 0.68594 | 11.4512 |  |  |  |  | 0.24 | 11.3298 | 0.11066 |  | 0.22813
11:26 | 4124 | 40 | 263.9 | 10.4 | 125 | 10.8025 | 0.68582 | 11.3805 |  |  |  |  | 0.25 | 12.3168 | 0.11823
11:26 | 4127 | 44 | 263.9 | 10.4 | 126 | 11.3298 | 0.68582 | 11.3088 |  |  |  |  | 0.26 | 12.3168 | 0.12317 |  | 0.25047
11:26 | 4128 | 52 | 263.9 | 10.4 | 127 | 12.3168 | 0.68582 | 11.2363 |  |  |  |  | 0.27 | 13.5571 | 0.12937
11:26 | 4126 | 52 | 263.9 | 10.4 | 128 | 12.3168 | 0.68582 | 11.1627 |  |  |  |  | 0.28 | 13.5571 | 0.13557 |  | 0.26818
11:26 | 4124 | 63 | 263.9 | 10.4 | 129 | 13.5571 | 0.68582 | 11.0883 |  |  |  |  | 0.29 | 12.6683 | 0.13113
11:26 | 4121 | 63 | 263.9 | 10.4 | 130 | 13.5571 | 0.68582 | 11.0128 |  |  |  |  | 0.3 | 12.4369 | 0.12553 |  | 0.24832
11:26 | 4117 | 55 | 264 | 10.4 | 131 | 12.6683 | 0.68569 | 10.9364 |  |  |  |  | 0.31 | 12.0798 | 0.12258
11:26 | 4117 | 53 | 264.1 | 10.4 | 132 | 12.4369 | 0.68556 | 10.859 |  |  |  |  | 0.32 | 11.7107 | 0.11895 |  | 0.23545
11:26 | 4127 | 50 | 264.1 | 10.4 | 133 | 12.0798 | 0.68556 | 10.7807 |  |  |  |  | 0.33 | 11.7107 | 0.11711
11:26 | 4127 | 47 | 264 | 10.4 | 134 | 11.7107 | 0.68569 | 10.7013 |  |  |  |  | 0.34 | 11.7107 | 0.11711 |  | 0.23421
11:26 | 4116 | 47 | 264 | 10.4 | 135 | 11.7107 | 0.68569 | 10.621 |  |  |  |  | 0.35 | 11.7107 | 0.11711
11:26 | 4113 | 47 | 264 | 10.4 | 136 | 11.7107 | 0.68569 | 10.5396 |  |  |  |  | 0.36 | 11.5855 | 0.11648 |  | 0.23213
11:26 | 4102 | 47 | 264 | 10.4 | 137 | 11.7107 | 0.68569 | 10.4572 |  |  |  |  | 0.37 | 11.5866 | 0.11586
11:26 | 4092 | 46 | 264 | 10.4 | 138 | 11.5855 | 0.68569 | 10.3738 |  |  |  |  | 0.38 | 11.334 | 0.1146 |  | 0.2271
11:26 | 4091 | 46 | 264.1 | 10.4 | 139 | 11.5866 | 0.68556 | 10.2894 |  |  |  |  | 0.39 | 11.2086 | 0.11271
11:26 | 4090 | 44 | 264.3 | 10.4 | 140 | 11.334 | 0.68531 | 10.204 |  |  |  |  | 0.4 | 10.8106 | 0.1101 |  | 0.21616
11:26 | 4089 | 43 | 264.7 | 10.4 | 141 | 11.2086 | 0.6848 | 10.1175 |  |  |  |  | 0.41 | 10.3973 | 0.10604
11:26 | 4077 | 40 | 264.7 | 10.3 | 142 | 10.8106 | 0.6848 | 10.03 |  |  |  |  | 0.42 | 10.1124 | 0.10255 |  | 0.2007
11:26 | 4077 | 37 | 264.7 | 10.3 | 143 | 10.3973 | 0.6848 | 9.9414 |  |  |  |  | 0.43 | 9.3631 | 0.097377
11:26 | 4078 | 35 | 264.7 | 10.3 | 144 | 10.1124 | 0.6848 | 9.8517 |  |  |  |  | 0.44 | 9.3631 | 0.093631 |  | 0.18566
11:26 | 4079 | 30 | 264.8 | 10.3 | 145 | 9.3631 | 0.68467 | 9.761 |  |  |  |  | 0.45 | 8.8826 | 0.091228
11:26 | 4074 | 30 | 264.8 | 10.3 | 146 | 9.3631 | 0.68467 | 9.6692 |  |  |  |  | 0.46 | 8.8818 | 0.088822 |  | 0.17764
11:26 | 4070 | 27 | 264.8 | 10.3 | 147 | 8.8826 | 0.68467 | 9.5764 |  |  |  |  | 0.47 | 8.8818 | 0.088818
11:26 | 4066 | 27 | 264.7 | 10.3 | 148 | 8.8818 | 0.6848 | 9.4824 |  |  |  |  | 0.48 | 8.8818 | 0.088818 |  | 0.17708
11:26 | 4059 | 27 | 264.7 | 10.3 | 149 | 8.8818 | 0.6848 | 9.3873 |  |  |  |  | 0.49 | 8.7158 | 0.087988
11:26 | 4059 | 27 | 264.7 | 10.3 | 150 | 8.8818 | 0.6848 | 9.2912 |  |  |  |  | 0.5 | 8.7149 | 0.087153 |  | 0.17485
11:26 | 4049 | 26 | 264.7 | 10.3 | 151 | 8.7158 | 0.6848 | 9.1939 |  |  |  |  | 0.51 | 8.881 | 0.087979
11:26 | 4049 | 26 | 264.6 | 10.3 | 152 | 8.7149 | 0.68492 | 9.0955 |  |  |  |  | 0.52 | 9.6666 | 0.092738 |  | 0.19071
11:26 | 4040 | 27 | 264.6 | 10.3 | 153 | 8.881 | 0.68492 | 8.996 |  |  |  |  | 0.53 | 9.6657 | 0.096661
11:26 | 4036 | 32 | 264.4 | 10.3 | 154 | 9.6666 | 0.68518 | 8.8954 |  |  |  |  | 0.54 | 8.8777 | 0.092717 |  | 0.18017
11:26 | 4037 | 32 | 264.3 | 10.4 | 155 | 9.6657 | 0.68531 | 8.7936 |  |  |  |  | 0.55 | 8.876 | 0.088768
11:26 | 4038 | 27 | 264.2 | 10.4 | 156 | 8.8777 | 0.68543 | 8.6906 |  |  |  |  | 0.56 | 8.8768 | 0.088764 |  | 0.17754
11:26 | 4043 | 27 | 264 | 10.4 | 157 | 8.876 | 0.68569 | 8.5866 |  |  |  |  | 0.57 | 8.8777 | 0.088772
11:26 | 4052 | 27 | 264.1 | 10.4 | 158 | 8.8768 | 0.68556 | 8.4813 |  |  |  |  | 0.58 | 9.3579 | 0.091178 |  | 0.18709
11:26 | 4052 | 27 | 264.2 | 10.4 | 159 | 8.8777 | 0.68543 | 8.3749 |  |  |  |  | 0.59 | 9.8164 | 0.095872
11:26 | 4054 | 30 | 264.2 | 10.4 | 160 | 9.3579 | 0.68543 | 8.2673 |  |  |  |  | 0.6 | 9.6666 | 0.097415 |  | 0.19065
11:26 | 4054 | 33 | 264.4 | 10.4 | 161 | 9.8164 | 0.68518 | 8.1585 |  |  |  |  | 0.61 | 8.7133 | 0.091899
11:26 | 4055 | 32 | 264.4 | 10.4 | 162 | 9.6666 | 0.68518 | 8.0486 |  |  |  |  | 0.62 | 8.7133 | 0.087133 |  | 0.17426
11:26 | 4055 | 26 | 264.4 | 10.4 | 163 | 8.7133 | 0.68518 | 7.9374 |  |  |  |  | 0.63 | 8.7125 | 0.087129
11:26 | 4056 | 26 | 264.4 | 10.4 | 164 | 8.7133 | 0.68518 | 7.8251 |  |  |  |  | 0.64 | 8.7125 | 0.087125 |  | 0.17311
11:26 | 4057 | 26 | 264.3 | 10.4 | 165 | 8.7125 | 0.68531 | 7.7115 |  |  |  |  | 0.65 | 8.3699 | 0.085412
11:26 | 4057 | 26 | 264.3 | 10.4 | 166 | 8.7125 | 0.68531 | 7.5967 |  |  |  |  | 0.66 | 8.3699 | 0.083699 |  | 0.16497
11:26 | 4059 | 24 | 264.2 | 10.4 | 167 | 8.3699 | 0.68543 | 7.4807 |  |  |  |  | 0.67 | 7.6407 | 0.080053
11:26 | 4059 | 24 | 264.2 | 10.4 | 168 | 8.3699 | 0.68543 | 7.3635 |  |  |  |  | 0.68 | 7.0457 | 0.073432 |  | 0.1429
11:26 | 4061 | 20 | 264.2 | 10.4 | 169 | 7.6407 | 0.68543 | 7.245 |  |  |  |  | 0.69 | 7.0457 | 0.070457
11:26 | 4061 | 17 | 264.4 | 10.4 | 170 | 7.0457 | 0.68518 | 7.1253 |  |  |  |  | 0.7 | 7.4479 | 0.072468 |  | 0.14695
11:26 | 4063 | 17 | 264.4 | 10.4 | 171 | 7.0457 | 0.68518 | 7.0043 |  |  |  |  | 0.71 | 7.2486 | 0.073482
11:26 | 4064 | 19 | 264.3 | 10.4 | 172 | 7.4479 | 0.68531 | 6.8821 |  |  |  |  | 0.72 | 6.6164 | 0.069325 |  | 0.13443
11:26 | 4065 | 18 | 264.2 | 10.4 | 173 | 7.2486 | 0.68543 | 6.7586 |  |  |  |  | 0.73 | 6.6158 | 0.066161
11:26 | 4066 | 15 | 264.1 | 10.4 | 174 | 6.6164 | 0.68556 | 6.6338 |  |  |  |  | 0.74 | 6.3915 | 0.065036 |  | 0.12857
11:26 | 4067 | 15 | 264 | 10.4 | 175 | 6.6158 | 0.68569 | 6.5077 |  |  |  |  | 0.75 | 6.3903 | 0.063909
11:26 | 4068 | 14 | 264 | 10.4 | 176 | 6.3915 | 0.68569 | 6.3804 |  |  |  |  | 0.76 | 6.1578 | 0.06274 |  | 0.12313
11:26 | 4069 | 14 | 263.8 | 10.4 | 177 | 6.3903 | 0.68594 | 6.2518 |  |  |  |  | 0.77 | 5.9168 | 0.060373
11:26 | 4071 | 13 | 263.8 | 10.4 | 178 | 6.1578 | 0.68594 | 6.1218 |  |  |  |  | 0.78 | 5.9168 | 0.059168 |  | 0.11833
11:26 | 4071 | 12 | 263.9 | 10.3 | 179 | 5.9168 | 0.68582 | 5.9906 |  |  |  |  | 0.79 | 5.9162 | 0.059165
11:26 | 4055 | 12 | 263.9 | 10.3 | 180 | 5.9168 | 0.68582 | 5.858 |  |  |  |  | 0.8 | 5.9157 | 0.05916 |  | 0.12207
11:26 | 4047 | 12 | 263.8 | 10.3 | 181 | 5.9162 | 0.68594 | 5.7241 |  |  |  |  | 0.81 | 7.0411 | 0.064784
11:26 | 4043 | 12 | 263.7 | 10.3 | 182 | 5.9157 | 0.68607 | 5.5889 |  |  |  |  | 0.82 | 7.0411 | 0.070411 |  | 0.13865
11:26 | 4039 | 17 | 263.7 | 10.3 | 183 | 7.0411 | 0.68607 | 5.4523 |  |  |  |  | 0.83 | 6.3897 | 0.067154
11:26 | 4036 | 17 | 263.7 | 10.3 | 184 | 7.0411 | 0.68607 | 5.3144 |  |  |  |  | 0.84 | 6.1572 | 0.062735 |  | 0.12227
11:26 | 4027 | 14 | 263.7 | 10.3 | 185 | 6.3897 | 0.68607 | 5.1752 |  |  |  |  | 0.85 | 5.6638 | 0.059105
11:26 | 4026 | 13 | 263.7 | 10.3 | 186 | 6.1572 | 0.68607 | 5.0346 |  |  |  |  | 0.86 | 5.1231 | 0.053935 |  | 0.10426
11:26 | 4010 | 11 | 263.7 | 10.3 | 187 | 5.6638 | 0.68607 | 4.8926 |  |  |  |  | 0.87 | 5.1231 | 0.051231
11:26 | 4010 | 9 | 263.7 | 10.3 | 188 | 5.1231 | 0.68607 | 4.7492 |  |  |  |  | 0.88 | 4.1822 | 0.046527 |  | 0.08678
11:26 | 4004 | 9 | 263.7 | 10.3 | 189 | 5.1231 | 0.68607 | 4.6045 |  |  |  |  | 0.89 | 4.1819 | 0.04182
11:26 | 4001 | 6 | 263.5 | 10.3 | 190 | 4.1822 | 0.68633 | 4.4584 |  |  |  |  | 0.9 | 2.957 | 0.035694 |  | 0.063224
11:26 | 4006 | 6 | 263.4 | 10.3 | 191 | 4.1819 | 0.68646 | 4.3109 |  |  |  |  | 0.91 | 2.9573 | 0.029572
11:26 | 4011 | 3 | 263.4 | 10.3 | 192 | 2.957 | 0.68646 | 4.162 |  |  |  |  | 0.92 | 2.4144 | 0.026858 |  | 0.04205
11:26 | 4016 | 3 | 263.5 | 10.3 | 193 | 2.9573 | 0.68633 | 4.0117 |  |  |  |  | 0.93 | 0 | 0.012072
11:26 | 4037 | 2 | 263.4 | 10.3 | 194 | 2.4144 | 0.68646 | 3.8599 |  |  |  |  | 0.94 | 1.7069 | 0.0085346 |  | 0.028449
11:26 | 4038 | 0 | 263.2 | 10.3 | 195 | 0 | 0.68671 | 3.7068 |  |  |  |  | 0.95 | 1.7069 | 0.017069
11:26 | 4050 | 1 | 263.2 | 10.3 | 196 | 1.7069 | 0.68671 | 3.5522 |  |  |  |  | 0.96 | 2.4139 | 0.020604 |  | 0.045921
11:26 | 4050 | 1 | 263.2 | 10.3 | 197 | 1.7069 | 0.68671 | 3.3961 |  |  |  |  | 0.97 | 2.4135 | 0.024137
11:26 | 4057 | 2 | 263.2 | 10.3 | 198 | 2.4139 | 0.68671 | 3.2387 |  |  |  |  | 0.98 | 2.4135 | 0.024135 |  | 0.040225
11:26 | 4061 | 2 | 263 | 10.3 | 199 | 2.4135 | 0.68697 | 3.0797 |  |  |  |  | 0.99 | 0 | 0.012067
11:26 | 4063 | 2 | 263 | 10.3 | 200 | 2.4135 | 0.68697 | 2.9194 |  |  |  |  | 1 | 0 | 0
11:26 | 4066 | 0 | 262.9 | 10.3 | 201 | 0 | 0.6871 | 2.7575
11:26 | 4065 | 0 | 262.9 | 10.3 | 202 | 0 | 0.6871 | 2.5942
11:26 | 4056 | 2 | 262.9 | 10.3 | 203 | 2.4133 | 0.6871 | 2.4294
11:26 | 4056 | 4 | 263 | 10.3 | 204 | 3.4132 | 0.68697 | 2.2631
11:26 | 4043 | 1 | 263 | 10.3 | 205 | 1.7066 | 0.68697 | 2.0953
11:26 | 4043 | -1 | 263.2 | 10.3 | 206 |  | 0.68671 | 1.9261
11:26 | 4055 | -1 | 263.2 | 10.3 | 207 |  | 0.68671 | 1.7553
11:26 | 4063 | -3 | 263.2 | 10.3 | 208 |  | 0.68671 | 1.583
11:26 | 4070 | -3 | 263.3 | 10.3 | 209 |  | 0.68658 | 1.4092
11:26 | 4076 | 6 | 263.3 | 10.3 | 210 | 4.1815 | 0.68658 | 1.2338
11:26 | 4076 | 6 | 263.4 | 10.3 |  |  | 0.68646
11:26 | 4075 | 5 | 263.4 | 10.3 |  |  | 0.68646
11:26 | 4075 | 5 | 263.3 | 10.3 |  |  | 0.68658
11:26 | 4075 | 8 | 263.3 | 10.3 |  |  | 0.68658
11:26 | 4075 | 11 | 263.3 | 10.3 |  |  | 0.68658
11:26 | 4071 | 11 | 263.3 | 10.4 |  |  | 0.68658
11:26 | 4068 | 10 | 263.3 | 10.4 |  |  | 0.68658
11:26 | 4068 | 10 | 263.3 | 10.4 |  |  | 0.68658
11:26 | 4068 | 6 | 263.4 | 10.4 |  |  | 0.68646
11:26 | 4069 | 6 | 263.4 | 10.4 |  |  | 0.68646
11:26 | 4076 | 4 | 263.4 | 10.4 |  |  | 0.68646
11:26 | 4076 | 2 | 263.3 | 10.4 |  |  | 0.68658
11:26 | 4084 | 1 | 263.3 | 10.4 |  |  | 0.68658
11:26 | 4084 | 1 | 263.4 | 10.4 |  |  | 0.68646
11:26 | 4089 | 1 | 263.4 | 10.3 |  |  | 0.68646
11:26 | 4094 | -1 | 263.4 | 10.3 |  |  | 0.68646
11:26 | 4101 | -1 | 263.5 | 10.4 |  |  | 0.68633
11:26 | 4107 | -2 | 263.6 | 10.4 |  |  | 0.6862
11:26 | 4108 | -2 | 263.8 | 10.4 |  |  | 0.68594
11:26 | 4127 | -1 | 263.8 | 10.4 |  |  | 0.68594
11:26 | 4127 | -1 | 263.9 | 10.4 |  |  | 0.68582
11:26 | 4139 | -2 | 263.9 | 10.4 |  |  | 0.68582
11:26 | 4139 | -4 | 263.9 | 10.4 |  |  | 0.68582
11:26 | 4143 | -4 | 263.9 | 10.4 |  |  | 0.68582
11:26 | 4147 | -2 | 263.9 | 10.4 |  |  | 0.68582
11:26 | 4147 | -2 | 263.9 | 10.4 |  |  | 0.68582
11:26 | 4147 | -2 | 263.9 | 10.4 |  |  | 0.68582
11:26 | 4147 | -2 | 264 | 10.4 |  |  | 0.68569
11:26 | 4146 | -2 | 264 | 10.4 |  |  | 0.68569
11:26 | 4146 | -2 | 264 | 10.4 |  |  | 0.68569
11:26 | 4140 | -2 | 264 | 10.4 |  |  | 0.68569
11:26 | 4140 | -2 | 263.9 | 10.4 |  |  | 0.68582
11:26 | 4140 | -2 | 263.9 | 10.4 |  |  | 0.68582
11:26 | 4140 | -2 | 263.9 | 10.4 |  |  | 0.68582
11:26 | 4142 | -2 | 263.9 | 10.4 |  |  | 0.68582
11:26 | 4144 | -1 | 263.8 | 10.4 |  |  | 0.68594
11:26 | 4143 | -1 | 263.8 | 10.4 |  |  | 0.68594
11:26 | 4136 | -2 | 263.8 | 10.4 |  |  | 0.68594
11:26 | 4136 | -2 | 263.8 | 10.4 |  |  | 0.68594
11:26 | 4143 | -3 | 263.8 | 10.4 |  |  | 0.68594
11:27 | 4143 | -5 | 263.9 | 10.4 |  |  | 0.68582
11:27 | 4139 | -4 | 263.9 | 10.4 |  |  | 0.68582
11:27 | 4136 | -2 | 264.1 | 10.4 |  |  | 0.68556
11:27 | 4137 | -2 | 264.2 | 10.3 |  |  | 0.68543
11:27 | 4139 | -1 | 264.2 | 10.3 |  |  | 0.68543
11:27 | 4139 | -1 | 264.2 | 10.3 |  |  | 0.68543
11:27 | 4139 | 3 | 264.2 | 10.3 |  |  | 0.68543
11:27 | 4139 | 7 | 264.4 | 10.3 |  |  | 0.68518
11:27 | 4131 | 7 | 264.4 | 10.4 |  |  | 0.68518
11:27 | 4131 | 6 | 264.3 | 10.4 |  |  | 0.68531
11:27 | 4130 | 6 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4129 | 7 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4124 | 7 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4119 | 8 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4119 | 8 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4120 | 8 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4120 | 7 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4123 | 6 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4123 | 5 | 264.2 | 10.3 |  |  | 0.68543
11:27 | 4124 | 5 | 264.2 | 10.3 |  |  | 0.68543
11:27 | 4124 | 2 | 264.1 | 10.3 |  |  | 0.68556
11:27 | 4128 | 2 | 264.1 | 10.3 |  |  | 0.68556
11:27 | 4133 | 10 | 264.1 | 10.3 |  |  | 0.68556
11:27 | 4133 | 11 | 263.9 | 10.4 |  |  | 0.68582
11:27 | 4131 | 13 | 264 | 10.4 |  |  | 0.68569
11:27 | 4131 | 15 | 264.2 | 10.4 |  |  | 0.68543
11:27 | 4113 | 15 | 264.2 | 10.4 |  |  | 0.68543
11:27 | 4111 | 15 | 264.2 | 10.4 |  |  | 0.68543
11:27 | 4111 | 15 | 264.2 | 10.3 |  |  | 0.68543
11:27 | 4110 | 13 | 264.2 | 10.3 |  |  | 0.68543
11:27 | 4106 | 13 | 264.2 | 10.3 |  |  | 0.68543
11:27 | 4100 | 15 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4100 | 15 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4097 | 15 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4097 | 15 | 264.2 | 10.3 |  |  | 0.68543
11:27 | 4087 | 14 | 264.2 | 10.3 |  |  | 0.68543
11:27 | 4085 | 12 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4085 | 12 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4085 | 6 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4087 | 6 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4090 | 6 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4090 | 6 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4099 | 7 | 264.3 | 10.3 |  |  | 0.68531
11:27 | 4099 | 7 | 264.2 | 10.4 |  |  | 0.68543
11:27 | 4103 | 8 | 264.2 | 10.4 |  |  | 0.68543
11:27 | 4104 | 10 | 264.4 | 10.4 |  |  | 0.68518
11:27 | 4106 | 10 | 264.5 | 10.4 |  |  | 0.68505
11:27 | 4107 | 14 | 264.5 | 10.4 |  |  | 0.68505
11:27 | 4105 | 14 | 264.6 | 10.4 |  |  | 0.68492
11:27 | 4101 | 17 | 264.6 | 10.4 |  |  | 0.68492
11:27 | 4101 | 18 | 264.6 | 10.4 |  |  | 0.68492
11:27 | 4101 | 15 | 264.6 | 10.4 |  |  | 0.68492
11:27 | 4101 | 12 | 264.6 | 10.4 |  |  | 0.68492
11:27 | 4102 | 11 | 264.6 | 10.4 |  |  | 0.68492
11:27 | 4102 | 8 | 264.5 | 10.4 |  |  | 0.68505
11:27 | 4103 | 9 | 264.5 | 10.4 |  |  | 0.68505
11:27 | 4103 | 17 | 264.4 | 10.4 |  |  | 0.68518
11:27 | 4109 | 17 | 264.4 | 10.4 |  |  | 0.68518
11:27 | 4121 | 27 | 264.3 | 10.4 |  |  | 0.68531
11:27 | 4121 | 30 | 264.1 | 10.4 |  |  | 0.68556
11:27 | 4119 | 33 | 264.1 | 10.4 |  |  | 0.68556
11:27 | 4119 | 35 | 264 | 10.4 |  |  | 0.68569
11:27 | 4118 | 35 | 264 | 10.4 |  |  | 0.68569
11:27 | 4117 | 32 | 263.9 | 10.4 |  |  | 0.68582
11:27 | 4123 | 32 | 263.9 | 10.4 |  |  | 0.68582
11:27 | 4127 | 26 | 263.7 | 10.4 |  |  | 0.68607
11:27 | 4125 | 26 | 263.6 | 10.3 |  |  | 0.6862
11:27 | 4120 | 34 | 263.6 | 10.3 |  |  | 0.6862
11:27 | 4120 | 37 | 263.6 | 10.3 |  |  | 0.6862
11:27 | 4119 | 40 | 263.6 | 10.4 |  |  | 0.6862
11:27 | 4119 | 44 | 263.6 | 10.3 |  |  | 0.6862
11:27 | 4120 | 44 | 263.6 | 10.3 |  |  | 0.6862
11:27 | 4120 | 45 | 264 | 10.3 |  |  | 0.68569
11:27 | 4113 | 46 | 264.1 | 10.3 |  |  | 0.68556
11:27 | 4106 | 52 | 264 | 10.3 |  |  | 0.68569
11:27 | 4098 | 52 | 263.9 | 10.3 |  |  | 0.68582
11:27 | 4082 | 44 | 263.9 | 10.3 |  |  | 0.68582
11:27 | 4081 | 41 | 263.9 | 10.3 |  |  | 0.68582
11:27 | 4070 | 38 | 263.9 | 10.3 |  |  | 0.68582
11:27 | 4070 | 35 | 263.7 | 10.3 |  |  | 0.68607
11:27 | 4061 | 36 | 263.7 | 10.3 |  |  | 0.68607
11:27 | 4058 | 39 | 263.8 | 10.3 |  |  | 0.68594
11:27 | 4057 | 40 | 263.8 | 10.3 |  |  | 0.68594
11:27 | 4056 | 43 | 263.8 | 10.3 |  |  | 0.68594
11:27 | 4054 | 43 | 263.8 | 10.3 |  |  | 0.68594
11:27 | 4052 | 43 | 263.8 | 10.3 |  |  | 0.68594
11:27 | 4052 | 43 | 263.8 | 10.3 |  |  | 0.68594
11:27 | 4055 | 39 | 263.8 | 10.3 |  |  | 0.68594
11:27 | 4055 | 36 | 263.6 | 10.3 |  |  | 0.6862
11:27 | 4071 | 39 | 263.6 | 10.3 |  |  | 0.6862
11:27 | 4077 | 50 | 263.6 | 10.3 |  |  | 0.6862
11:27 | 4077 | 50 | 263.7 | 10.3 |  |  | 0.68607
11:27 | 4076 | 59 | 263.6 | 10.3 |  |  | 0.6862
11:27 | 4073 | 59 | 263.5 | 10.3 |  |  | 0.68633
11:27 | 4064 | 54 | 263.6 | 10.3 |  |  | 0.6862
11:27 | 4064 | 52 | 263.7 | 10.3 |  |  | 0.68607
11:27 | 4063 | 48 | 263.7 | 10.3 |  |  | 0.68607
11:27 | 4063 | 45 | 263.5 | 10.3 |  |  | 0.68633
11:27 | 4062 | 45 | 263.5 | 10.3 |  |  | 0.68633
11:27 | 4062 | 46 | 263.5 | 10.3 |  |  | 0.68633
11:27 | 4063 | 46 | 263.4 | 10.3 |  |  | 0.68646
11:27 | 4065 | 57 | 263.3 | 10.3 |  |  | 0.68658
11:27 | 4067 | 57 | 263.2 | 10.3 |  |  | 0.68671
11:27 | 4074 | 62 | 263.2 | 10.3 |  |  | 0.68671
11:27 | 4074 | 64 | 263.2 | 10.3 |  |  | 0.68671
11:27 | 4078 | 65 | 263.2 | 10.3 |  |  | 0.68671
11:27 | 4078 | 67 | 262.6 | 10.3 |  |  | 0.68748
11:27 | 4078 | 68 | 262.6 | 10.3 |  |  | 0.68748
11:27 | 4078 | 73 | 262.7 | 10.3 |  |  | 0.68735
11:27 | 4080 | 73 | 262.7 | 10.3 |  |  | 0.68735
11:27 | 4082 | 75 | 262.8 | 10.3 |  |  | 0.68722
11:27 | 4083 | 75 | 262.8 | 10.3 |  |  | 0.68722
11:27 | 4084 | 67 | 262.8 | 10.3 |  |  | 0.68722
11:27 | 4086 | 62 | 263 | 10.3 |  |  | 0.68697
11:27 | 4124 | 59 | 263 | 10.3 |  |  | 0.68697
11:27 | 4124 | 56 | 263.1 | 10.3 |  |  | 0.68684
11:27 | 4124 | 55 | 263.1 | 10.3 |  |  | 0.68684
11:27 | 4124 | 51 | 263.2 | 10.3 |  |  | 0.68671
11:27 | 4125 | 51 | 263.2 | 10.3 |  |  | 0.68671
11:27 | 4127 | 50 | 263.3 | 10.3 |  |  | 0.68658
11:27 | 4127 | 50 | 263.3 | 10.3 |  |  | 0.68658
11:27 | 4128 | 53 | 263.3 | 10.3 |  |  | 0.68658
11:27 | 4127 | 55 | 263.2 | 10.3 |  |  | 0.68671
11:27 | 4119 | 57 | 263.2 | 10.3 |  |  | 0.68671
11:27 | 4119 | 59 | 263.4 | 10.3 |  |  | 0.68646
11:27 | 4119 | 59 | 263.4 | 10.3 |  |  | 0.68646
11:27 | 4118 | 67 | 263.3 | 10.3 |  |  | 0.68658
11:27 | 4118 | 67 | 263.2 | 10.3 |  |  | 0.68671
11:27 | 4117 | 72 | 263.4 | 10.3 |  |  | 0.68646
11:27 | 4116 | 72 | 263.5 | 10.3 |  |  | 0.68633
11:27 | 4107 | 72 | 263.5 | 10.3 |  |  | 0.68633
11:27 | 4107 | 72 | 263.5 | 10.3 |  |  | 0.68633
11:27 | 4097 | 73 | 263.5 | 10.3 |  |  | 0.68633
11:27 | 4097 | 75 | 263.5 | 10.3 |  |  | 0.68633
11:27 | 4099 | 75 | 263.5 | 10.3 |  |  | 0.68633
11:27 | 4101 | 81 | 263.5 | 10.3 |  |  | 0.68633
11:27 | 4109 | 81 | 263.5 | 10.3 |  |  | 0.68633
11:27 | 4117 | 76 | 263.7 | 10.3 |  |  | 0.68607
11:27 | 4120 | 76 | 263.8 | 10.4 |  |  | 0.68594
11:27 | 4144 | 76 | 263.8 | 10.4 |  |  | 0.68594
11:27 | 4144 | 76 | 263.8 | 10.4 |  |  | 0.68594
11:27 | 4157 | 79 | 263.8 | 10.4 |  |  | 0.68594
11:27 | 4157 | 82 | 263.8 | 10.4 |  |  | 0.68594
11:27 | 4158 | 82 | 263.8 | 10.4 |  |  | 0.68594
11:27 | 4159 | 78 | 264 | 10.4 |  |  | 0.68569
11:27 | 4157 | 78 | 264.1 | 10.5 |  |  | 0.68556
11:27 | 4155 | 80 | 264 | 10.5 |  |  | 0.68569
11:27 | 4155 | 80 | 264 | 10.5 |  |  | 0.68569
11:27 | 4158 | 77 | 264 | 10.5 |  |  | 0.68569
11:27 | 4159 | 75 | 264.1 | 10.4 |  |  | 0.68556
11:27 | 4170 | 72 | 264.1 | 10.4 |  |  | 0.68556
11:27 | 4170 | 69 | 264.1 | 10.4 |  |  | 0.68556
11:27 | 4170 | 69 | 264.1 | 10.4 |  |  | 0.68556
11:27 | 4169 | 82 | 264 | 10.4 |  |  | 0.68569
11:27 | 4161 | 82 | 263.9 | 10.4 |  |  | 0.68582
11:27 | 4152 | 73 | 264 | 10.4 |  |  | 0.68569
11:27 | 4152 | 73 | 264.1 | 10.4 |  |  | 0.68556
11:27 | 4149 | 74 | 264.1 | 10.4 |  |  | 0.68556
11:27 | 4149 | 76 | 263.8 | 10.4 |  |  | 0.68594
11:27 | 4141 | 82 | 263.8 | 10.4 |  |  | 0.68594
11:27 | 4141 | 87 | 263.9 | 10.4 |  |  | 0.68582
11:27 | 4133 | 87 | 263.9 | 10.4 |  |  | 0.68582
11:27 | 4127 | 84 | 263.9 | 10.4 |  |  | 0.68582
11:27 | 4131 | 84 | 263.8 | 10.4 |  |  | 0.68594
11:27 | 4136 | 93 | 263.7 | 10.4 |  |  | 0.68607
11:27 | 4136 | 93 | 263.6 | 10.4 |  |  | 0.6862
11:27 | 4138 | 91 | 263.7 | 10.4 |  |  | 0.68607
11:27 | 4138 | 90 | 263.9 | 10.4 |  |  | 0.68582
11:27 | 4131 | 86 | 263.9 | 10.5 |  |  | 0.68582
11:27 | 4131 | 83 | 263.8 | 10.5 |  |  | 0.68594
11:27 | 4128 | 82 | 263.8 | 10.4 |  |  | 0.68594
11:27 | 4127 | 78 | 263.8 | 10.4 |  |  | 0.68594
11:27 | 4128 | 78 | 263.9 | 10.4 |  |  | 0.68582
11:27 | 4130 | 75 | 263.7 | 10.4 |  |  | 0.68607
11:27 | 4131 | 75 | 263.5 | 10.4 |  |  | 0.68633
11:27 | 4150 | 71 | 263.5 | 10.4 |  |  | 0.68633
11:27 | 4150 | 68 | 263.7 | 10.4 |  |  | 0.68607
11:27 | 4162 | 68 | 263.7 | 10.4 |  |  | 0.68607
11:27 | 4163 | 67 | 263.7 | 10.4 |  |  | 0.68607
11:27 | 4163 | 67 | 263.7 | 10.4 |  |  | 0.68607
11:27 | 4164 | 71 | 264.1 | 10.4 |  |  | 0.68556
11:27 | 4163 | 71 | 264.4 | 10.4 |  |  | 0.68518
11:27 | 4161 | 74 | 264.4 | 10.4 |  |  | 0.68518
11:27 | 4160 | 74 | 264.5 | 10.4 |  |  | 0.68505
11:27 | 4145 | 76 | 264.5 | 10.4 |  |  | 0.68505

## P5
| Port | 5
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current
| Pa | Pa | Deg C | mA
Averages | 4044.8383 | 26.3811 | 261.1494 | 10.3614 | [11 empty] | 6.7964 |  | 6.9904
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current |  |  |  |  | a | b | n | h | xi | f(xi) | Aj
| Pa. | Pa | Deg C | mA |  | 8.5765 |  |  | 0 | 1 | 100 | 0.01 | 0 | 12.1568
[6 empty] | vel | dens | [5 empty] | 0.01 | 13.0756 | 0.12616 |  | 0.26025
11:29 | 4069 | 51 | 260.3 | 10.4 | 1 | 12.1568 | 0.69044 | 13.8186 |  |  |  |  | 0.02 | 13.6158 | 0.13346
11:29 | 4060 | 59 | 260.3 | 10.4 | 2 | 13.0756 | 0.69044 | 13.7929 |  |  |  |  | 0.03 | 13.7218 | 0.13669 |  | 0.27443
11:29 | 4060 | 64 | 260.1 | 10.4 | 3 | 13.6158 | 0.6907 | 13.7669 |  |  |  |  | 0.04 | 13.8256 | 0.13774
11:29 | 4050 | 65 | 260.1 | 10.4 | 4 | 13.7218 | 0.6907 | 13.7407 |  |  |  |  | 0.05 | 13.8256 | 0.13826 |  | 0.27722
11:29 | 4050 | 66 | 260 | 10.4 | 5 | 13.8256 | 0.69083 | 13.7142 |  |  |  |  | 0.06 | 14.0375 | 0.13932
11:29 | 4051 | 66 | 260 | 10.4 | 6 | 13.8256 | 0.69083 | 13.6875 |  |  |  |  | 0.07 | 13.9365 | 0.13987 |  | 0.27802
11:29 | 4051 | 68 | 260.3 | 10.4 | 7 | 14.0375 | 0.69044 | 13.6605 |  |  |  |  | 0.08 | 13.6222 | 0.13779
11:29 | 4053 | 67 | 260.5 | 10.4 | 8 | 13.9365 | 0.69018 | 13.6332 |  |  |  |  | 0.09 | 13.6235 | 0.13623 |  | 0.27175
11:29 | 4055 | 64 | 260.6 | 10.4 | 9 | 13.6222 | 0.69006 | 13.6057 |  |  |  |  | 0.1 | 13.4089 | 0.13516
11:29 | 4056 | 64 | 260.7 | 10.4 | 10 | 13.6235 | 0.68993 | 13.5778 |  |  |  |  | 0.11 | 13.3028 | 0.13356 |  | 0.26641
11:29 | 4060 | 62 | 260.7 | 10.4 | 11 | 13.4089 | 0.68993 | 13.5497 |  |  |  |  | 0.12 | 13.3028 | 0.13303
11:29 | 4060 | 61 | 260.9 | 10.4 | 12 | 13.3028 | 0.68967 | 13.5214 |  |  |  |  | 0.13 | 13.3003 | 0.13302 |  | 0.26602
11:29 | 4058 | 61 | 260.9 | 10.4 | 13 | 13.3028 | 0.68967 | 13.4927 |  |  |  |  | 0.14 | 13.3003 | 0.133
11:29 | 4058 | 61 | 260.7 | 10.4 | 14 | 13.3003 | 0.68993 | 13.4638 |  |  |  |  | 0.15 | 13.3003 | 0.133 |  | 0.26601
11:29 | 4059 | 61 | 260.7 | 10.4 | 15 | 13.3003 | 0.68993 | 13.4346 |  |  |  |  | 0.16 | 13.3003 | 0.133
11:29 | 4059 | 61 | 260.7 | 10.4 | 16 | 13.3003 | 0.68993 | 13.4051 |  |  |  |  | 0.17 | 13.3003 | 0.133 |  | 0.26601
11:29 | 4057 | 61 | 260.7 | 10.4 | 17 | 13.3003 | 0.68993 | 13.3754 |  |  |  |  | 0.18 | 13.3003 | 0.133
11:29 | 4055 | 61 | 260.7 | 10.4 | 18 | 13.3003 | 0.68993 | 13.3453 |  |  |  |  | 0.19 | 13.1909 | 0.13246 |  | 0.26419
11:29 | 4055 | 61 | 260.7 | 10.3 | 19 | 13.3003 | 0.68993 | 13.315 |  |  |  |  | 0.2 | 13.1921 | 0.13191
11:29 | 4061 | 60 | 260.7 | 10.3 | 20 | 13.1909 | 0.68993 | 13.2844 |  |  |  |  | 0.21 | 12.8581 | 0.13025 |  | 0.25753
11:29 | 4061 | 60 | 260.8 | 10.3 | 21 | 13.1921 | 0.6898 | 13.2535 |  |  |  |  | 0.22 | 12.6352 | 0.12747
11:29 | 4077 | 57 | 260.8 | 10.3 | 22 | 12.8581 | 0.6898 | 13.2223 |  |  |  |  | 0.23 | 12.6352 | 0.12635 |  | 0.25602
11:29 | 4077 | 55 | 261.2 | 10.3 | 23 | 12.6352 | 0.68928 | 13.1909 |  |  |  |  | 0.24 | 13.6298 | 0.13133
11:29 | 4081 | 55 | 261.2 | 10.3 | 24 | 12.6352 | 0.68928 | 13.1591 |  |  |  |  | 0.25 | 13.6298 | 0.1363 |  | 0.27331
11:29 | 4083 | 64 | 261.2 | 10.3 | 25 | 13.6298 | 0.68928 | 13.127 |  |  |  |  | 0.26 | 13.8438 | 0.13737
11:29 | 4076 | 64 | 261.2 | 10.4 | 26 | 13.6298 | 0.68928 | 13.0947 |  |  |  |  | 0.27 | 13.8464 | 0.13845 |  | 0.27657
11:29 | 4068 | 66 | 261.4 | 10.4 | 27 | 13.8438 | 0.68902 | 13.0621 |  |  |  |  | 0.28 | 13.7411 | 0.13794
11:29 | 4067 | 66 | 261.6 | 10.4 | 28 | 13.8464 | 0.68877 | 13.0291 |  |  |  |  | 0.29 | 13.6349 | 0.13688 |  | 0.27305
11:29 | 4062 | 65 | 261.6 | 10.4 | 29 | 13.7411 | 0.68877 | 12.9959 |  |  |  |  | 0.3 | 13.6349 | 0.13635
11:29 | 4062 | 64 | 261.6 | 10.4 | 30 | 13.6349 | 0.68877 | 12.9624 |  |  |  |  | 0.31 | 13.6337 | 0.13634 |  | 0.27268
11:29 | 4057 | 64 | 261.6 | 10.4 | 31 | 13.6349 | 0.68877 | 12.9285 |  |  |  |  | 0.32 | 13.6337 | 0.13634
11:29 | 4057 | 64 | 261.5 | 10.4 | 32 | 13.6337 | 0.68889 | 12.8944 |  |  |  |  | 0.33 | 13.2007 | 0.13417 |  | 0.26546
11:29 | 4064 | 64 | 261.5 | 10.4 | 33 | 13.6337 | 0.68889 | 12.86 |  |  |  |  | 0.34 | 13.2007 | 0.13201
11:29 | 4070 | 60 | 261.5 | 10.4 | 34 | 13.2007 | 0.68889 | 12.8253 |  |  |  |  | 0.35 | 13.2007 | 0.13201 |  | 0.26401
11:29 | 4075 | 60 | 261.5 | 10.4 | 35 | 13.2007 | 0.68889 | 12.7902 |  |  |  |  | 0.36 | 13.1995 | 0.132
11:29 | 4081 | 60 | 261.5 | 10.4 | 36 | 13.2007 | 0.68889 | 12.7549 |  |  |  |  | 0.37 | 12.8653 | 0.13032 |  | 0.25728
11:29 | 4080 | 60 | 261.4 | 10.4 | 37 | 13.1995 | 0.68902 | 12.7192 |  |  |  |  | 0.38 | 12.5222 | 0.12694
11:29 | 4073 | 57 | 261.4 | 10.4 | 38 | 12.8653 | 0.68902 | 12.6833 |  |  |  |  | 0.39 | 12.9777 | 0.1275 |  | 0.25949
11:29 | 4073 | 54 | 261.4 | 10.4 | 39 | 12.5222 | 0.68902 | 12.647 |  |  |  |  | 0.4 | 13.4152 | 0.13196
11:29 | 4070 | 58 | 261.4 | 10.4 | 40 | 12.9777 | 0.68902 | 12.6104 |  |  |  |  | 0.41 | 13.4152 | 0.13415 |  | 0.27042
11:29 | 4070 | 62 | 261.2 | 10.4 | 41 | 13.4152 | 0.68928 | 12.5735 |  |  |  |  | 0.42 | 14.0493 | 0.13732
11:29 | 4067 | 62 | 261.2 | 10.4 | 42 | 13.4152 | 0.68928 | 12.5363 |  |  |  |  | 0.43 | 14.0506 | 0.1405 |  | 0.27668
11:29 | 4065 | 68 | 261.2 | 10.4 | 43 | 14.0493 | 0.68928 | 12.4988 |  |  |  |  | 0.44 | 12.7507 | 0.13401
11:29 | 4062 | 68 | 261.3 | 10.4 | 44 | 14.0506 | 0.68915 | 12.4609 |  |  |  |  | 0.45 | 12.6364 | 0.12694 |  | 0.25234
11:29 | 4058 | 56 | 261.3 | 10.4 | 45 | 12.7507 | 0.68915 | 12.4228 |  |  |  |  | 0.46 | 12.4045 | 0.1252
11:29 | 4059 | 55 | 261.3 | 10.4 | 46 | 12.6364 | 0.68915 | 12.3843 |  |  |  |  | 0.47 | 12.1671 | 0.12286 |  | 0.24333
11:29 | 4063 | 53 | 261.3 | 10.4 | 47 | 12.4045 | 0.68915 | 12.3455 |  |  |  |  | 0.48 | 11.9261 | 0.12047
11:29 | 4063 | 51 | 261.2 | 10.4 | 48 | 12.1671 | 0.68928 | 12.3064 |  |  |  |  | 0.49 | 11.4279 | 0.11677 |  | 0.23022
11:29 | 4047 | 49 | 261.2 | 10.4 | 49 | 11.9261 | 0.68928 | 12.267 |  |  |  |  | 0.5 | 11.4268 | 0.11427
11:29 | 4046 | 45 | 261.1 | 10.4 | 50 | 11.4279 | 0.68941 | 12.2272 |  |  |  |  | 0.51 | 11.5531 | 0.1149 |  | 0.23064
11:29 | 4037 | 45 | 261 | 10.4 | 51 | 11.4268 | 0.68954 | 12.1871 |  |  |  |  | 0.52 | 11.552 | 0.11553
11:29 | 4027 | 46 | 261 | 10.4 | 52 | 11.5531 | 0.68954 | 12.1467 |  |  |  |  | 0.53 | 10.6368 | 0.11094 |  | 0.21533
11:29 | 4019 | 46 | 260.9 | 10.4 | 53 | 11.552 | 0.68967 | 12.1059 |  |  |  |  | 0.54 | 10.4996 | 0.10568
11:29 | 4007 | 39 | 260.9 | 10.4 | 54 | 10.6368 | 0.68967 | 12.0648 |  |  |  |  | 0.55 | 10.7723 | 0.10636 |  | 0.21543
11:29 | 4007 | 38 | 260.9 | 10.4 | 55 | 10.4996 | 0.68967 | 12.0234 |  |  |  |  | 0.56 | 11.0394 | 0.10906
11:29 | 4012 | 40 | 260.9 | 10.4 | 56 | 10.7723 | 0.68967 | 11.9817 |  |  |  |  | 0.57 | 11.5531 | 0.11296 |  | 0.23216
11:29 | 4012 | 42 | 261 | 10.4 | 57 | 11.0394 | 0.68954 | 11.9396 |  |  |  |  | 0.58 | 12.3964 | 0.11975
11:29 | 4017 | 46 | 261 | 10.4 | 58 | 11.5531 | 0.68954 | 11.8972 |  |  |  |  | 0.59 | 12.3964 | 0.12396 |  | 0.24713
11:29 | 4017 | 53 | 260.6 | 10.4 | 59 | 12.3964 | 0.69006 | 11.8545 |  |  |  |  | 0.6 | 12.158 | 0.12277
11:29 | 4022 | 53 | 260.6 | 10.4 | 60 | 12.3964 | 0.69006 | 11.8114 |  |  |  |  | 0.61 | 12.158 | 0.12158 |  | 0.24394
11:29 | 4026 | 51 | 260.4 | 10.4 | 61 | 12.158 | 0.69031 | 11.7679 |  |  |  |  | 0.62 | 12.3917 | 0.12275
11:29 | 4026 | 51 | 260.4 | 10.4 | 62 | 12.158 | 0.69031 | 11.7242 |  |  |  |  | 0.63 | 12.5057 | 0.12449 |  | 0.24816
11:29 | 4027 | 53 | 260.2 | 10.4 | 63 | 12.3917 | 0.69057 | 11.6801 |  |  |  |  | 0.64 | 12.0337 | 0.1227
11:29 | 4028 | 54 | 260 | 10.4 | 64 | 12.5057 | 0.69083 | 11.6356 |  |  |  |  | 0.65 | 11.795 | 0.11914 |  | 0.23545
11:29 | 4030 | 50 | 260 | 10.4 | 65 | 12.0337 | 0.69083 | 11.5908 |  |  |  |  | 0.66 | 11.4204 | 0.11608
11:29 | 4030 | 48 | 260.4 | 10.4 | 66 | 11.795 | 0.69031 | 11.5457 |  |  |  |  | 0.67 | 10.7673 | 0.11094 |  | 0.21752
11:29 | 4024 | 45 | 260.4 | 10.4 | 67 | 11.4204 | 0.69031 | 11.5002 |  |  |  |  | 0.68 | 10.7673 | 0.10767
11:29 | 4024 | 40 | 260.4 | 10.4 | 68 | 10.7673 | 0.69031 | 11.4544 |  |  |  |  | 0.69 | 10.2138 | 0.10491 |  | 0.20612
11:29 | 4023 | 40 | 260.4 | 10.4 | 69 | 10.7673 | 0.69031 | 11.4082 |  |  |  |  | 0.7 | 10.2138 | 0.10214
11:29 | 4022 | 36 | 260.3 | 10.4 | 70 | 10.2138 | 0.69044 | 11.3616 |  |  |  |  | 0.71 | 9.3247 | 0.097693 |  | 0.18894
11:29 | 4026 | 36 | 260.3 | 10.4 | 71 | 10.2138 | 0.69044 | 11.3147 |  |  |  |  | 0.72 | 9.1689 | 0.092468
11:29 | 4031 | 30 | 260.4 | 10.4 | 72 | 9.3247 | 0.69031 | 11.2675 |  |  |  |  | 0.73 | 9.9279 | 0.095484 |  | 0.19792
11:29 | 4031 | 29 | 260.5 | 10.4 | 73 | 9.1689 | 0.69018 | 11.2199 |  |  |  |  | 0.74 | 10.4966 | 0.10212
11:29 | 4039 | 34 | 260.5 | 10.4 | 74 | 9.9279 | 0.69018 | 11.1719 |  |  |  |  | 0.75 | 10.4966 | 0.10497 |  | 0.21039
11:29 | 4039 | 38 | 260.6 | 10.4 | 75 | 10.4966 | 0.69006 | 11.1236 |  |  |  |  | 0.76 | 10.6338 | 0.10565
11:29 | 4039 | 38 | 260.6 | 10.4 | 76 | 10.4966 | 0.69006 | 11.0749 |  |  |  |  | 0.77 | 10.6338 | 0.10634 |  | 0.20832
11:29 | 4039 | 39 | 260.6 | 10.4 | 77 | 10.6338 | 0.69006 | 11.0259 |  |  |  |  | 0.78 | 9.3274 | 0.099806
11:29 | 4031 | 39 | 260.6 | 10.4 | 78 | 10.6338 | 0.69006 | 10.9765 |  |  |  |  | 0.79 | 9.3282 | 0.093278 |  | 0.18857
11:29 | 4024 | 30 | 260.7 | 10.4 | 79 | 9.3274 | 0.68993 | 10.9267 |  |  |  |  | 0.8 | 9.9307 | 0.096294
11:29 | 4027 | 30 | 260.8 | 10.4 | 80 | 9.3282 | 0.6898 | 10.8766 |  |  |  |  | 0.81 | 10.0747 | 0.10003 |  | 0.20004
11:29 | 4031 | 34 | 260.8 | 10.4 | 81 | 9.9307 | 0.6898 | 10.8261 |  |  |  |  | 0.82 | 9.7826 | 0.099286
11:29 | 4032 | 35 | 260.7 | 10.4 | 82 | 10.0747 | 0.68993 | 10.7753 |  |  |  |  | 0.83 | 9.6314 | 0.09707 |  | 0.19508
11:29 | 4043 | 33 | 260.7 | 10.4 | 83 | 9.7826 | 0.68993 | 10.724 |  |  |  |  | 0.84 | 10.2157 | 0.099236
11:29 | 4043 | 32 | 260.5 | 10.4 | 84 | 9.6314 | 0.69018 | 10.6724 |  |  |  |  | 0.85 | 11.1648 | 0.1069 |  | 0.22013
11:29 | 4051 | 36 | 260.5 | 10.4 | 85 | 10.2157 | 0.69018 | 10.6205 |  |  |  |  | 0.86 | 11.1648 | 0.11165
11:29 | 4053 | 43 | 260.5 | 10.4 | 86 | 11.1648 | 0.69018 | 10.5681 |  |  |  |  | 0.87 | 11.5477 | 0.11356 |  | 0.22968
11:29 | 4046 | 43 | 260.5 | 10.4 | 87 | 11.1648 | 0.69018 | 10.5154 |  |  |  |  | 0.88 | 11.5477 | 0.11548
11:29 | 4040 | 46 | 260.5 | 10.4 | 88 | 11.5477 | 0.69018 | 10.4623 |  |  |  |  | 0.89 | 12.0404 | 0.11794 |  | 0.23957
11:29 | 4034 | 46 | 260.5 | 10.4 | 89 | 11.5477 | 0.69018 | 10.4089 |  |  |  |  | 0.9 | 12.1625 | 0.12101
11:29 | 4025 | 50 | 260.6 | 10.4 | 90 | 12.0404 | 0.69006 | 10.355 |  |  |  |  | 0.91 | 11.6758 | 0.11919 |  | 0.23345
11:29 | 4024 | 51 | 260.8 | 10.4 | 91 | 12.1625 | 0.6898 | 10.3008 |  |  |  |  | 0.92 | 11.169 | 0.11422
11:29 | 4010 | 47 | 260.8 | 10.4 | 92 | 11.6758 | 0.6898 | 10.2462 |  |  |  |  | 0.93 | 11.2981 | 0.11234 |  | 0.22596
11:29 | 4010 | 43 | 260.9 | 10.4 | 93 | 11.169 | 0.68967 | 10.1912 |  |  |  |  | 0.94 | 11.4268 | 0.11362
11:29 | 4008 | 44 | 260.9 | 10.4 | 94 | 11.2981 | 0.68967 | 10.1358 |  |  |  |  | 0.95 | 11.4268 | 0.11427 |  | 0.23059
11:29 | 4007 | 45 | 261 | 10.4 | 95 | 11.4268 | 0.68954 | 10.0801 |  |  |  |  | 0.96 | 12.0427 | 0.11735
11:29 | 4016 | 45 | 261 | 10.4 | 96 | 11.4268 | 0.68954 | 10.0239 |  |  |  |  | 0.97 | 12.0404 | 0.12042 |  | 0.23918
11:29 | 4025 | 50 | 260.8 | 10.4 | 97 | 12.0427 | 0.6898 | 9.9674 |  |  |  |  | 0.98 | 11.5499 | 0.11795
11:29 | 4025 | 50 | 260.6 | 10.4 | 98 | 12.0404 | 0.69006 | 9.9105 |  |  |  |  | 0.99 | 11.4258 | 0.11488 |  | 0.2272
11:29 | 4025 | 46 | 260.7 | 10.4 | 99 | 11.5499 | 0.68993 | 9.8532 |  |  |  |  | 1 | 10.9061 | 0.11166
11:29 | 4025 | 45 | 260.9 | 10.4 | 100 | 11.4258 | 0.68967 | 9.7955 |  |  |  |  | 0 | 10.5005 | -10.7033 |  | -10.3927
11:29 | 4028 | 41 | 260.9 | 10.4 | 101 | 10.9061 | 0.68967 | 9.7374 |  |  |  |  | 0.01 | 10.0775 | 0.10289
11:29 | 4028 | 38 | 261 | 10.4 | 102 | 10.5005 | 0.68954 | 9.6789 |  |  |  |  | 0.02 | 9.1749 | 0.096262 |  | 0.18651
11:29 | 4011 | 35 | 261 | 10.4 | 103 | 10.0775 | 0.68954 | 9.62 |  |  |  |  | 0.03 | 9.1749 | 0.091749
11:29 | 4007 | 29 | 261.2 | 10.4 | 104 | 9.1749 | 0.68928 | 9.5608 |  |  |  |  | 0.04 | 8.3481 | 0.087615 |  | 0.16972
11:29 | 4001 | 29 | 261.2 | 10.4 | 105 | 9.1749 | 0.68928 | 9.5011 |  |  |  |  | 0.05 | 8.3489 | 0.083485
11:29 | 3996 | 24 | 261.4 | 10.4 | 106 | 8.3481 | 0.68902 | 9.441 |  |  |  |  | 0.06 | 7.026 | 0.076874 |  | 0.14351
11:29 | 3999 | 24 | 261.5 | 10.4 | 107 | 8.3489 | 0.68889 | 9.3806 |  |  |  |  | 0.07 | 6.5991 | 0.068126
11:29 | 4004 | 17 | 261.4 | 10.4 | 108 | 7.026 | 0.68902 | 9.3197 |  |  |  |  | 0.08 | 6.3754 | 0.064873 |  | 0.12825
11:29 | 4005 | 15 | 261.3 | 10.4 | 109 | 6.5991 | 0.68915 | 9.2584 |  |  |  |  | 0.09 | 6.3754 | 0.063754
11:29 | 4016 | 14 | 261.3 | 10.4 | 110 | 6.3754 | 0.68915 | 9.1967 |  |  |  |  | 0.1 | 6.3754 | 0.063754 |  | 0.12897
11:29 | 4016 | 14 | 261.3 | 10.4 | 111 | 6.3754 | 0.68915 | 9.1346 |  |  |  |  | 0.11 | 6.8156 | 0.065955
11:29 | 4018 | 14 | 261.3 | 10.4 | 112 | 6.3754 | 0.68915 | 9.0721 |  |  |  |  | 0.12 | 6.8156 | 0.068156 |  | 0.14083
11:29 | 4018 | 16 | 261.3 | 10.4 | 113 | 6.8156 | 0.68915 | 9.0092 |  |  |  |  | 0.13 | 8.17 | 0.074928
11:29 | 4018 | 16 | 261.3 | 10.4 | 114 | 6.8156 | 0.68915 | 8.9459 |  |  |  |  | 0.14 | 8.1685 | 0.081693 |  | 0.16724
11:29 | 4017 | 23 | 261.1 | 10.4 | 115 | 8.17 | 0.68941 | 8.8822 |  |  |  |  | 0.15 | 9.3291 | 0.087488
11:29 | 4017 | 23 | 260.9 | 10.4 | 116 | 8.1685 | 0.68967 | 8.8181 |  |  |  |  | 0.16 | 9.6341 | 0.094816 |  | 0.19116
11:29 | 4016 | 30 | 260.9 | 10.4 | 117 | 9.3291 | 0.68967 | 8.7535 |  |  |  |  | 0.17 | 9.4833 | 0.095587
11:29 | 4016 | 32 | 260.8 | 10.4 | 118 | 9.6341 | 0.6898 | 8.6885 |  |  |  |  | 0.18 | 9.3308 | 0.094071 |  | 0.18713
11:29 | 4030 | 31 | 260.9 | 10.4 | 119 | 9.4833 | 0.68967 | 8.6231 |  |  |  |  | 0.19 | 9.3308 | 0.093308
11:29 | 4030 | 30 | 261.1 | 10.4 | 120 | 9.3308 | 0.68941 | 8.5573 |  |  |  |  | 0.2 | 9.636 | 0.094834 |  | 0.1917
11:29 | 4035 | 30 | 261.1 | 10.4 | 121 | 9.3308 | 0.68941 | 8.4911 |  |  |  |  | 0.21 | 9.6351 | 0.096355
11:29 | 4037 | 32 | 261 | 10.4 | 122 | 9.636 | 0.68954 | 8.4245 |  |  |  |  | 0.22 | 9.0136 | 0.093243 |  | 0.18234
11:29 | 4038 | 32 | 260.9 | 10.4 | 123 | 9.6351 | 0.68967 | 8.3574 |  |  |  |  | 0.23 | 9.0136 | 0.090136
11:29 | 4039 | 28 | 261 | 10.4 | 124 | 9.0136 | 0.68954 | 8.2899 |  |  |  |  | 0.24 | 8.8512 | 0.089324 |  | 0.17702
11:29 | 4040 | 28 | 261 | 10.4 | 125 | 9.0136 | 0.68954 | 8.222 |  |  |  |  | 0.25 | 8.6865 | 0.087689
11:29 | 4041 | 27 | 261 | 10.4 | 126 | 8.8512 | 0.68954 | 8.1537 |  |  |  |  | 0.26 | 8.3458 | 0.085162 |  | 0.16687
11:29 | 4041 | 26 | 261.1 | 10.4 | 127 | 8.6865 | 0.68941 | 8.0849 |  |  |  |  | 0.27 | 7.992 | 0.081689
11:29 | 4043 | 24 | 261.1 | 10.4 | 128 | 8.3458 | 0.68941 | 8.0157 |  |  |  |  | 0.28 | 7.8082 | 0.079001 |  | 0.15347
11:29 | 4043 | 22 | 261.3 | 10.4 | 129 | 7.992 | 0.68915 | 7.9461 |  |  |  |  | 0.29 | 6.8149 | 0.073116
11:29 | 4045 | 21 | 261.3 | 10.4 | 130 | 7.8082 | 0.68915 | 7.8761 |  |  |  |  | 0.3 | 6.8149 | 0.068149 |  | 0.13898
11:29 | 4046 | 16 | 261.2 | 10.4 | 131 | 6.8149 | 0.68928 | 7.8056 |  |  |  |  | 0.31 | 7.6186 | 0.072168
11:29 | 4047 | 16 | 261.2 | 10.4 | 132 | 6.8149 | 0.68928 | 7.7346 |  |  |  |  | 0.32 | 7.6179 | 0.076182 |  | 0.15478
11:29 | 4049 | 20 | 261.1 | 10.4 | 133 | 7.6186 | 0.68941 | 7.6633 |  |  |  |  | 0.33 | 8.345 | 0.079814
11:29 | 4045 | 20 | 261 | 10.4 | 134 | 7.6179 | 0.68954 | 7.5915 |  |  |  |  | 0.34 | 8.5179 | 0.084314 |  | 0.16678
11:29 | 4035 | 24 | 261 | 10.4 | 135 | 8.345 | 0.68954 | 7.5193 |  |  |  |  | 0.35 | 7.6186 | 0.080682
11:29 | 4034 | 25 | 261.1 | 10.4 | 136 | 8.5179 | 0.68941 | 7.4466 |  |  |  |  | 0.36 | 6.8149 | 0.072168 |  | 0.14036
11:29 | 4021 | 20 | 261.1 | 10.4 | 137 | 7.6186 | 0.68941 | 7.3735 |  |  |  |  | 0.37 | 7.2283 | 0.070216
11:29 | 4021 | 16 | 261.2 | 10.4 | 138 | 6.8149 | 0.68928 | 7.2999 |  |  |  |  | 0.38 | 8.5179 | 0.078731 |  | 0.16606
11:29 | 4024 | 18 | 261.2 | 10.4 | 139 | 7.2283 | 0.68928 | 7.2259 |  |  |  |  | 0.39 | 8.5171 | 0.085175
11:29 | 4026 | 25 | 261.1 | 10.4 | 140 | 8.5179 | 0.68941 | 7.1515 |  |  |  |  | 0.4 | 8.3458 | 0.084314 |  | 0.16749
11:29 | 4022 | 25 | 261 | 10.4 | 141 | 8.5171 | 0.68954 | 7.0766 |  |  |  |  | 0.41 | 8.3458 | 0.083458
11:29 | 4019 | 24 | 261.1 | 10.4 | 142 | 8.3458 | 0.68941 | 7.0013 |  |  |  |  | 0.42 | 7.8075 | 0.080766 |  | 0.15732
11:29 | 4020 | 24 | 261.1 | 10.4 | 143 | 8.3458 | 0.68941 | 6.9255 |  |  |  |  | 0.43 | 7.6193 | 0.077134
11:29 | 4023 | 21 | 261.2 | 10.4 | 144 | 7.8075 | 0.68928 | 6.8493 |  |  |  |  | 0.44 | 7.6193 | 0.076193 |  | 0.15301
11:29 | 4023 | 20 | 261.2 | 10.4 | 145 | 7.6193 | 0.68928 | 6.7726 |  |  |  |  | 0.45 | 7.806 | 0.077127
11:29 | 4024 | 20 | 261.2 | 10.4 | 146 | 7.6193 | 0.68928 | 6.6955 |  |  |  |  | 0.46 | 7.6179 | 0.07712 |  | 0.15298
11:29 | 4024 | 21 | 261 | 10.4 | 147 | 7.806 | 0.68954 | 6.6179 |  |  |  |  | 0.47 | 7.6179 | 0.076179
11:29 | 4013 | 20 | 261 | 10.4 | 148 | 7.6179 | 0.68954 | 6.5398 |  |  |  |  | 0.48 | 7.4243 | 0.075211 |  | 0.14563
11:29 | 4008 | 20 | 261 | 10.4 | 149 | 7.6179 | 0.68954 | 6.4613 |  |  |  |  | 0.49 | 6.373 | 0.068986
11:29 | 3995 | 19 | 260.9 | 10.4 | 150 | 7.4243 | 0.68967 | 6.3824 |  |  |  |  | 0.5 | 6.373 | 0.06373 |  | 0.12588
11:29 | 3983 | 14 | 260.9 | 10.4 | 151 | 6.373 | 0.68967 | 6.3029 |  |  |  |  | 0.51 | 5.9002 | 0.061366
11:29 | 3980 | 14 | 260.9 | 10.4 | 152 | 6.373 | 0.68967 | 6.2231 |  |  |  |  | 0.52 | 5.3862 | 0.056432 |  | 0.10754
11:29 | 3965 | 12 | 260.9 | 10.4 | 153 | 5.9002 | 0.68967 | 6.1427 |  |  |  |  | 0.53 | 4.8175 | 0.051018
11:29 | 3965 | 10 | 260.9 | 10.4 | 154 | 5.3862 | 0.68967 | 6.0619 |  |  |  |  | 0.54 | 4.5068 | 0.046622 |  | 0.091172
11:29 | 3962 | 8 | 260.9 | 10.4 | 155 | 4.8175 | 0.68967 | 5.9807 |  |  |  |  | 0.55 | 4.5068 | 0.045068
11:29 | 3962 | 7 | 261 | 10.4 | 156 | 4.5068 | 0.68954 | 5.8989 |  |  |  |  | 0.56 | 4.818 | 0.046624 |  | 0.095322
11:29 | 3960 | 7 | 261 | 10.4 | 157 | 4.5068 | 0.68954 | 5.8167 |  |  |  |  | 0.57 | 4.818 | 0.04818
11:29 | 3959 | 8 | 261 | 10.4 | 158 | 4.818 | 0.68954 | 5.7341 |  |  |  |  | 0.58 | 2.9507 | 0.038843 |  | 0.065238
11:29 | 3955 | 8 | 261 | 10.3 | 159 | 4.818 | 0.68954 | 5.6509 |  |  |  |  | 0.59 | 2.9507 | 0.029507
11:29 | 3952 | 3 | 261.1 | 10.3 | 160 | 2.9507 | 0.68941 | 5.5673 |  |  |  |  | 0.6 | 3.4071 | 0.031789 |  | 0.067963
11:29 | 3953 | 3 | 261.1 | 10.3 | 161 | 2.9507 | 0.68941 | 5.4832 |  |  |  |  | 0.61 | 3.8097 | 0.036084
11:29 | 3960 | 4 | 261.1 | 10.3 | 162 | 3.4071 | 0.68941 | 5.3987 |  |  |  |  | 0.62 | 4.5076 | 0.041587 |  | 0.088864
11:29 | 3960 | 5 | 261.2 | 10.3 | 163 | 3.8097 | 0.68928 | 5.3136 |  |  |  |  | 0.63 | 4.8189 | 0.046633
11:29 | 3965 | 7 | 261.2 | 10.3 | 164 | 4.5076 | 0.68928 | 5.2281 |  |  |  |  | 0.64 | 4.8189 | 0.048189 |  | 0.09534
11:29 | 3965 | 8 | 261.2 | 10.3 | 165 | 4.8189 | 0.68928 | 5.1421 |  |  |  |  | 0.65 | 4.5076 | 0.046633
11:29 | 3964 | 8 | 261.2 | 10.3 | 166 | 4.8189 | 0.68928 | 5.0557 |  |  |  |  | 0.66 | 4.5081 | 0.045079 |  | 0.090161
11:29 | 3963 | 7 | 261.2 | 10.3 | 167 | 4.5076 | 0.68928 | 4.9687 |  |  |  |  | 0.67 | 4.5085 | 0.045083
11:29 | 3968 | 7 | 261.3 | 10.3 | 168 | 4.5081 | 0.68915 | 4.8813 |  |  |  |  | 0.68 | 4.5085 | 0.045085 |  | 0.09398
11:29 | 3973 | 7 | 261.4 | 10.3 | 169 | 4.5085 | 0.68902 | 4.7934 |  |  |  |  | 0.69 | 5.6517 | 0.050801
11:29 | 3972 | 7 | 261.4 | 10.3 | 170 | 4.5085 | 0.68902 | 4.705 |  |  |  |  | 0.7 | 6.1446 | 0.058982 |  | 0.12045
11:30 | 3969 | 11 | 261.4 | 10.3 | 171 | 5.6517 | 0.68902 | 4.6161 |  |  |  |  | 0.71 | 5.9036 | 0.060241
11:30 | 3968 | 13 | 261.5 | 10.3 | 172 | 6.1446 | 0.68889 | 4.5267 |  |  |  |  | 0.72 | 5.6522 | 0.057779 |  | 0.11388
11:30 | 3955 | 12 | 261.5 | 10.3 | 173 | 5.9036 | 0.68889 | 4.4369 |  |  |  |  | 0.73 | 5.6522 | 0.056522
11:30 | 3955 | 11 | 261.5 | 10.3 | 174 | 5.6522 | 0.68889 | 4.3465 |  |  |  |  | 0.74 | 4.8207 | 0.052365 |  | 0.099185
11:30 | 3949 | 11 | 261.5 | 10.3 | 175 | 5.6522 | 0.68889 | 4.2557 |  |  |  |  | 0.75 | 4.8207 | 0.048207
11:30 | 3944 | 8 | 261.6 | 10.3 | 176 | 4.8207 | 0.68877 | 4.1644 |  |  |  |  | 0.76 | 3.8111 | 0.043159 |  | 0.079587
11:30 | 3942 | 8 | 261.6 | 10.3 | 177 | 4.8207 | 0.68877 | 4.0725 |  |  |  |  | 0.77 | 3.8111 | 0.038111
11:30 | 3940 | 5 | 261.6 | 10.3 | 178 | 3.8111 | 0.68877 | 3.9802 |  |  |  |  | 0.78 | 2.4103 | 0.031107 |  | 0.044841
11:30 | 3941 | 5 | 261.6 | 10.2 | 179 | 3.8111 | 0.68877 | 3.8874 |  |  |  |  | 0.79 | 0 | 0.012052
11:30 | 3954 | 2 | 261.6 | 10.2 | 180 | 2.4103 | 0.68877 | 3.7941 |  |  |  |  | 0.8 | 0 | 0 |  | 0
11:30 | 3955 | 0 | 261.6 | 10.2 | 181 | 0 | 0.68877 | 3.7003 |  |  |  |  | 0.81 | 0 | 0
11:30 | 3984 | 0 | 261.6 | 10.2 | 182 | 0 | 0.68877 | 3.606 |  |  |  |  | 0.82 | 0 | 0 |  | 0
11:30 | 3984 | 0 | 261.6 | 10.2 | 183 | 0 | 0.68877 | 3.5111 |  |  |  |  | 0.83 | 0 | 0
11:30 | 3992 | 0 | 261.6 | 10.2 | 184 | 0 | 0.68877 | 3.4158 |  |  |  |  | 0.84 | 0 | 0 |  | 0
11:30 | 3999 | 0 | 261.5 | 10.2 | 185 | 0 | 0.68889 | 3.32 |  |  |  |  | 0.85 | 0 | 0
11:30 | 3991 | 0 | 261.5 | 10.2 | 186 | 0 | 0.68889 | 3.2237 |  |  |  |  | 0.86 | 0 | 0 |  | 0
11:30 | 3982 | 0 | 261.5 | 10.2 | 187 | 0 | 0.68889 | 3.1268 |  |  |  |  | 0.87 | 0 | 0
11:30 | 3983 | 0 | 261.4 | 10.2 | 188 | 0 | 0.68902 | 3.0295 |  |  |  |  | 0.88 | 0 | 0 |  | 0
11:30 | 3984 | 0 | 261.4 | 10.2 | 189 | 0 | 0.68902 | 2.9316 |  |  |  |  | 0.89 | 0 | 0
11:30 | 3984 | 0 | 261.6 | 10.2 | 190 | 0 | 0.68877 | 2.8333 |  |  |  |  | 0.9 | 0 | 0 |  | 0
11:30 | 3973 | 0 | 261.6 | 10.2 | 191 | 0 | 0.68877 | 2.7344 |  |  |  |  | 0.91 | 0 | 0
11:30 | 3973 | 0 | 261.6 | 10.2 | 192 | 0 | 0.68877 | 2.635 |  |  |  |  | 0.92 | 0 | 0 |  | 0
11:30 | 3976 | 0 | 261.6 | 10.2 | 193 | 0 | 0.68877 | 2.5351 |  |  |  |  | 0.93 | 0 | 0
11:30 | 3979 | 0 | 261.6 | 10.2 | 194 | 0 | 0.68877 | 2.4347 |  |  |  |  | 0.94 | 0 | 0 |  | 0
11:30 | 3979 | 0 | 261.5 | 10.2 | 195 | 0 | 0.68889 | 2.3337 |  |  |  |  | 0.95 | 0 | 0
11:30 | 3978 | 0 | 261.5 | 10.2 | 196 | 0 | 0.68889 | 2.2323 |  |  |  |  | 0.96 | 0 | 0 |  | 0
11:30 | 3978 | 0 | 261.5 | 10.2 | 197 | 0 | 0.68889 | 2.1303 |  |  |  |  | 0.97 | 0 | 0
11:30 | 3979 | 0 | 261.5 | 10.2 | 198 | 0 | 0.68889 | 2.0278 |  |  |  |  | 0.98 | 0 | 0 |  | 0
11:30 | 3979 | 0 | 261.3 | 10.3 | 199 | 0 | 0.68915 | 1.9248 |  |  |  |  | 0.99 | 0 | 0
11:30 | 3985 | 0 | 261.3 | 10.3 | 200 | 0 | 0.68915 | 1.8212 |  |  |  |  | 1 | 0 | 0
11:30 | 3985 | 0 | 261.1 | 10.3 | 201 | 0 | 0.68941 | 1.7171
11:30 | 3984 | 0 | 261.1 | 10.2 | 202 | 0 | 0.68941 | 1.6125
11:30 | 3984 | 0 | 261.2 | 10.2 | 203 | 0 | 0.68928 | 1.5074
11:30 | 3991 | 0 | 261.3 | 10.2 | 204 | 0 | 0.68915 | 1.4017
11:30 | 3998 | 0 | 261.2 | 10.2 | 205 | 0 | 0.68928 | 1.2955
11:30 | 4000 | 0 | 261.1 | 10.2 | 206 |  | 0.68941 | 1.1888
11:30 | 4017 | 0 | 261.1 | 10.2 | 207 |  | 0.68941 | 1.0815
11:30 | 4017 | 0 | 260.8 | 10.3 | 208 |  | 0.6898 | 0.97375
11:30 | 4029 | 0 | 260.8 | 10.3 | 209 |  | 0.6898 | 0.86542
11:30 | 4030 | 0 | 260.6 | 10.3 | 210 | 0 | 0.69006 | 0.75655
11:30 | 4026 | 0 | 260.6 | 10.3 |  |  | 0.69006
11:30 | 4023 | -1 | 260.6 | 10.3 |  |  | 0.69006
11:30 | 4020 | -1 | 260.6 | 10.3 |  |  | 0.69006
11:30 | 4017 | -1 | 260.6 | 10.3 |  |  | 0.69006
11:30 | 4017 | -1 | 260.6 | 10.3 |  |  | 0.69006
11:30 | 4019 | -3 | 260.6 | 10.3 |  |  | 0.69006
11:30 | 4019 | -6 | 260.5 | 10.3 |  |  | 0.69018
11:30 | 4045 | -6 | 260.5 | 10.3 |  |  | 0.69018
11:30 | 4047 | -6 | 260.2 | 10.3 |  |  | 0.69057
11:30 | 4050 | -6 | 260.1 | 10.3 |  |  | 0.6907
11:30 | 4053 | -3 | 260.1 | 10.3 |  |  | 0.6907
11:30 | 4052 | -3 | 260.1 | 10.3 |  |  | 0.6907
11:30 | 4052 | -4 | 260 | 10.3 |  |  | 0.69083
11:30 | 4052 | -4 | 259.9 | 10.4 |  |  | 0.69096
11:30 | 4049 | -4 | 259.9 | 10.4 |  |  | 0.69096
11:30 | 4049 | -3 | 260 | 10.4 |  |  | 0.69083
11:30 | 4045 | -3 | 260 | 10.4 |  |  | 0.69083
11:30 | 4045 | -3 | 259.8 | 10.4 |  |  | 0.69109
11:30 | 4045 | -3 | 259.8 | 10.4 |  |  | 0.69109
11:30 | 4045 | -6 | 259.9 | 10.4 |  |  | 0.69096
11:30 | 4049 | -6 | 260 | 10.3 |  |  | 0.69083
11:30 | 4055 | -4 | 260 | 10.3 |  |  | 0.69083
11:30 | 4054 | -4 | 260 | 10.3 |  |  | 0.69083
11:30 | 4047 | -2 | 260 | 10.3 |  |  | 0.69083
11:30 | 4047 | -1 | 260.1 | 10.3 |  |  | 0.6907
11:30 | 4036 | -1 | 260.1 | 10.3 |  |  | 0.6907
11:30 | 4035 | -1 | 260.1 | 10.3 |  |  | 0.6907
11:30 | 4026 | -1 | 260.1 | 10.3 |  |  | 0.6907
11:30 | 4018 | -1 | 260.1 | 10.3 |  |  | 0.6907
11:30 | 4012 | -1 | 260.1 | 10.3 |  |  | 0.6907
11:30 | 4003 | -3 | 260 | 10.3 |  |  | 0.69083
11:30 | 4004 | -3 | 259.9 | 10.3 |  |  | 0.69096
11:30 | 4014 | -4 | 259.9 | 10.3 |  |  | 0.69096
11:30 | 4014 | -5 | 259.9 | 10.3 |  |  | 0.69096
11:30 | 4016 | -4 | 259.9 | 10.3 |  |  | 0.69096
11:30 | 4017 | -3 | 259.9 | 10.3 |  |  | 0.69096
11:30 | 4019 | -3 | 259.9 | 10.3 |  |  | 0.69096
11:30 | 4021 | -3 | 260 | 10.3 |  |  | 0.69083
11:30 | 4021 | -3 | 260.1 | 10.3 |  |  | 0.6907
11:30 | 4022 | -2 | 260 | 10.3 |  |  | 0.69083
11:30 | 4023 | -2 | 260 | 10.2 |  |  | 0.69083
11:30 | 4032 | -3 | 260 | 10.2 |  |  | 0.69083
11:30 | 4032 | -5 | 260 | 10.2 |  |  | 0.69083
11:30 | 4057 | -5 | 260 | 10.2 |  |  | 0.69083
11:30 | 4062 | -5 | 260.1 | 10.2 |  |  | 0.6907
11:30 | 4066 | -5 | 260.1 | 10.2 |  |  | 0.6907
11:30 | 4069 | -4 | 260.1 | 10.2 |  |  | 0.6907
11:30 | 4072 | -4 | 260.1 | 10.3 |  |  | 0.6907
11:30 | 4077 | -4 | 260.1 | 10.3 |  |  | 0.6907
11:30 | 4076 | -4 | 260.3 | 10.3 |  |  | 0.69044
11:30 | 4072 | -3 | 260.3 | 10.3 |  |  | 0.69044
11:30 | 4072 | -2 | 260.3 | 10.3 |  |  | 0.69044
11:30 | 4070 | -2 | 260.3 | 10.3 |  |  | 0.69044
11:30 | 4070 | -2 | 260.4 | 10.3 |  |  | 0.69031
11:30 | 4074 | -2 | 260.4 | 10.3 |  |  | 0.69031
11:30 | 4078 | -2 | 260.4 | 10.3 |  |  | 0.69031
11:30 | 4076 | -2 | 260.4 | 10.3 |  |  | 0.69031
11:30 | 4073 | -2 | 260.4 | 10.3 |  |  | 0.69031
11:30 | 4072 | -2 | 260.3 | 10.3 |  |  | 0.69044
11:30 | 4063 | -2 | 260.3 | 10.3 |  |  | 0.69044
11:30 | 4063 | -2 | 260.6 | 10.3 |  |  | 0.69006
11:30 | 4061 | -2 | 260.6 | 10.3 |  |  | 0.69006
11:30 | 4060 | -3 | 260.6 | 10.3 |  |  | 0.69006
11:30 | 4062 | -3 | 260.6 | 10.3 |  |  | 0.69006
11:30 | 4063 | -2 | 260.6 | 10.3 |  |  | 0.69006
11:30 | 4064 | -2 | 260.6 | 10.4 |  |  | 0.69006
11:30 | 4066 | -3 | 260.6 | 10.4 |  |  | 0.69006
11:30 | 4068 | -3 | 260.7 | 10.4 |  |  | 0.68993
11:30 | 4094 | -3 | 260.7 | 10.4 |  |  | 0.68993
11:30 | 4094 | -3 | 260.7 | 10.4 |  |  | 0.68993
11:30 | 4099 | -2 | 260.7 | 10.4 |  |  | 0.68993
11:30 | 4101 | 2 | 260.8 | 10.4 |  |  | 0.6898
11:30 | 4090 | 2 | 260.8 | 10.4 |  |  | 0.6898
11:30 | 4079 | 2 | 260.9 | 10.4 |  |  | 0.68967
11:30 | 4074 | 2 | 260.9 | 10.4 |  |  | 0.68967
11:30 | 4061 | 3 | 261 | 10.4 |  |  | 0.68954
11:30 | 4060 | 4 | 261.2 | 10.3 |  |  | 0.68928
11:30 | 4053 | 1 | 261.2 | 10.3 |  |  | 0.68928
11:30 | 4053 | -1 | 261 | 10.3 |  |  | 0.68954
11:30 | 4066 | -2 | 261 | 10.3 |  |  | 0.68954
11:30 | 4071 | -5 | 261 | 10.3 |  |  | 0.68954
11:30 | 4080 | -5 | 261 | 10.3 |  |  | 0.68954
11:30 | 4088 | -2 | 261 | 10.3 |  |  | 0.68954
11:30 | 4089 | -2 | 261 | 10.3 |  |  | 0.68954
11:30 | 4091 | 5 | 261 | 10.3 |  |  | 0.68954
11:30 | 4091 | 8 | 261.1 | 10.3 |  |  | 0.68941
11:30 | 4082 | 8 | 261.1 | 10.3 |  |  | 0.68941
11:30 | 4082 | 8 | 261.4 | 10.3 |  |  | 0.68902
11:30 | 4079 | 8 | 261.4 | 10.3 |  |  | 0.68902
11:30 | 4077 | 9 | 261.4 | 10.3 |  |  | 0.68902
11:30 | 4074 | 9 | 261.5 | 10.3 |  |  | 0.68889
11:30 | 4070 | 8 | 261.4 | 10.3 |  |  | 0.68902
11:30 | 4074 | 8 | 261.4 | 10.4 |  |  | 0.68902
11:30 | 4083 | 10 | 261.4 | 10.4 |  |  | 0.68902
11:30 | 4083 | 10 | 261.6 | 10.4 |  |  | 0.68877
11:30 | 4083 | 12 | 261.6 | 10.4 |  |  | 0.68877
11:30 | 4083 | 14 | 261.6 | 10.4 |  |  | 0.68877
11:30 | 4080 | 14 | 261.6 | 10.4 |  |  | 0.68877
11:30 | 4079 | 13 | 261.7 | 10.4 |  |  | 0.68864
11:30 | 4076 | 14 | 261.8 | 10.4 |  |  | 0.68851
11:30 | 4073 | 21 | 261.7 | 10.4 |  |  | 0.68864
11:30 | 4072 | 21 | 261.6 | 10.4 |  |  | 0.68877
11:30 | 4066 | 26 | 261.6 | 10.4 |  |  | 0.68877
11:30 | 4066 | 29 | 261.8 | 10.3 |  |  | 0.68851
11:30 | 4076 | 24 | 261.8 | 10.3 |  |  | 0.68851
11:30 | 4076 | 20 | 261.8 | 10.3 |  |  | 0.68851
11:30 | 4082 | 20 | 261.8 | 10.4 |  |  | 0.68851
11:30 | 4085 | 21 | 261.8 | 10.4 |  |  | 0.68851
11:30 | 4077 | 21 | 261.9 | 10.4 |  |  | 0.68838
11:30 | 4070 | 14 | 261.9 | 10.4 |  |  | 0.68838
11:30 | 4069 | 14 | 261.9 | 10.4 |  |  | 0.68838
11:30 | 4066 | 15 | 261.9 | 10.4 |  |  | 0.68838
11:30 | 4066 | 16 | 261.7 | 10.4 |  |  | 0.68864
11:30 | 4068 | 15 | 261.7 | 10.4 |  |  | 0.68864
11:30 | 4068 | 15 | 261.9 | 10.4 |  |  | 0.68838
11:30 | 4067 | 15 | 261.9 | 10.4 |  |  | 0.68838
11:30 | 4066 | 15 | 261.8 | 10.4 |  |  | 0.68851
11:30 | 4077 | 15 | 261.8 | 10.4 |  |  | 0.68851
11:30 | 4086 | 24 | 261.9 | 10.4 |  |  | 0.68838
11:30 | 4083 | 24 | 262 | 10.4 |  |  | 0.68825
11:30 | 4072 | 25 | 262 | 10.4 |  |  | 0.68825
11:30 | 4071 | 25 | 262.1 | 10.4 |  |  | 0.68812
11:30 | 4048 | 27 | 262.1 | 10.4 |  |  | 0.68812
11:30 | 4048 | 28 | 262.1 | 10.4 |  |  | 0.68812
11:30 | 4048 | 28 | 262.1 | 10.5 |  |  | 0.68812
11:30 | 4048 | 32 | 262 | 10.5 |  |  | 0.68825
11:30 | 4049 | 32 | 262 | 10.5 |  |  | 0.68825
11:30 | 4049 | 37 | 262 | 10.5 |  |  | 0.68825
11:30 | 4051 | 37 | 262 | 10.4 |  |  | 0.68825
11:30 | 4066 | 33 | 262 | 10.4 |  |  | 0.68825
11:30 | 4067 | 30 | 261.9 | 10.4 |  |  | 0.68838
11:30 | 4090 | 32 | 261.9 | 10.4 |  |  | 0.68838
11:30 | 4090 | 34 | 262.1 | 10.4 |  |  | 0.68812
11:30 | 4092 | 33 | 262.1 | 10.4 |  |  | 0.68812
11:30 | 4093 | 30 | 262.2 | 10.4 |  |  | 0.68799
11:30 | 4092 | 30 | 262.2 | 10.4 |  |  | 0.68799
11:30 | 4092 | 31 | 262.4 | 10.4 |  |  | 0.68774
11:30 | 4091 | 31 | 262.5 | 10.4 |  |  | 0.68761
11:30 | 4088 | 32 | 262.5 | 10.4 |  |  | 0.68761
11:30 | 4088 | 33 | 262.5 | 10.4 |  |  | 0.68761
11:30 | 4088 | 31 | 262.5 | 10.4 |  |  | 0.68761
11:30 | 4088 | 29 | 262.4 | 10.4 |  |  | 0.68774
11:30 | 4090 | 29 | 262.4 | 10.4 |  |  | 0.68774
11:30 | 4092 | 26 | 262.3 | 10.4 |  |  | 0.68786
11:30 | 4085 | 26 | 262.1 | 10.4 |  |  | 0.68812
11:30 | 4077 | 23 | 262.2 | 10.4 |  |  | 0.68799
11:30 | 4077 | 23 | 262.2 | 10.4 |  |  | 0.68799
11:30 | 4071 | 29 | 262.2 | 10.4 |  |  | 0.68799
11:30 | 4071 | 34 | 262 | 10.4 |  |  | 0.68825
11:30 | 4053 | 33 | 262 | 10.4 |  |  | 0.68825
11:30 | 4053 | 32 | 262.3 | 10.4 |  |  | 0.68786
11:30 | 4047 | 32 | 262.3 | 10.4 |  |  | 0.68786
11:30 | 4042 | 24 | 262.2 | 10.4 |  |  | 0.68799
11:30 | 4047 | 24 | 262 | 10.4 |  |  | 0.68825
11:30 | 4051 | 28 | 262 | 10.4 |  |  | 0.68825
11:30 | 4051 | 28 | 262 | 10.4 |  |  | 0.68825
11:30 | 4048 | 26 | 261.9 | 10.4 |  |  | 0.68838
11:30 | 4048 | 23 | 261.6 | 10.4 |  |  | 0.68877
11:30 | 4037 | 24 | 261.6 | 10.4 |  |  | 0.68877
11:30 | 4037 | 24 | 261.6 | 10.4 |  |  | 0.68877
11:30 | 4028 | 25 | 261.6 | 10.4 |  |  | 0.68877
11:30 | 4022 | 36 | 261.7 | 10.4 |  |  | 0.68864
11:30 | 4020 | 36 | 261.8 | 10.4 |  |  | 0.68851
11:30 | 4019 | 42 | 261.8 | 10.4 |  |  | 0.68851
11:30 | 4019 | 42 | 261.8 | 10.4 |  |  | 0.68851
11:30 | 4027 | 40 | 261.8 | 10.4 |  |  | 0.68851
11:30 | 4027 | 38 | 261.4 | 10.4 |  |  | 0.68902
11:30 | 4039 | 42 | 261.4 | 10.4 |  |  | 0.68902
11:30 | 4039 | 45 | 261.5 | 10.4 |  |  | 0.68889
11:30 | 4041 | 46 | 261.5 | 10.3 |  |  | 0.68889
11:30 | 4044 | 52 | 261.5 | 10.3 |  |  | 0.68889
11:30 | 4037 | 52 | 261.4 | 10.3 |  |  | 0.68902
11:30 | 4030 | 51 | 261.3 | 10.3 |  |  | 0.68915
11:30 | 4029 | 51 | 261.1 | 10.4 |  |  | 0.68941
11:30 | 4025 | 55 | 261.1 | 10.4 |  |  | 0.68941
11:30 | 4025 | 57 | 260.9 | 10.4 |  |  | 0.68967
11:30 | 4034 | 60 | 260.9 | 10.4 |  |  | 0.68967
11:30 | 4035 | 64 | 261.2 | 10.4 |  |  | 0.68928
11:30 | 4044 | 64 | 261.2 | 10.3 |  |  | 0.68928
11:30 | 4052 | 54 | 261.3 | 10.3 |  |  | 0.68915
11:30 | 4066 | 54 | 261.4 | 10.4 |  |  | 0.68902
11:30 | 4081 | 48 | 261.4 | 10.4 |  |  | 0.68902
11:30 | 4082 | 47 | 261.4 | 10.4 |  |  | 0.68902
11:30 | 4094 | 50 | 261.5 | 10.4 |  |  | 0.68889
11:30 | 4094 | 52 | 261.6 | 10.4 |  |  | 0.68877
11:30 | 4091 | 50 | 261.6 | 10.4 |  |  | 0.68877
11:30 | 4091 | 46 | 261.6 | 10.4 |  |  | 0.68877
11:30 | 4092 | 46 | 261.6 | 10.4 |  |  | 0.68877
11:30 | 4093 | 44 | 261.7 | 10.4 |  |  | 0.68864
11:30 | 4099 | 44 | 261.8 | 10.3 |  |  | 0.68851
11:30 | 4106 | 47 | 261.7 | 10.3 |  |  | 0.68864
11:30 | 4107 | 47 | 261.7 | 10.4 |  |  | 0.68864
11:30 | 4120 | 47 | 261.7 | 10.4 |  |  | 0.68864
11:30 | 4120 | 47 | 261.7 | 10.4 |  |  | 0.68864
11:30 | 4128 | 50 | 261.7 | 10.4 |  |  | 0.68864
11:30 | 4129 | 53 | 261.9 | 10.4 |  |  | 0.68838
11:30 | 4127 | 53 | 262 | 10.4 |  |  | 0.68825
11:30 | 4124 | 49 | 261.9 | 10.4 |  |  | 0.68838
11:30 | 4128 | 49 | 261.9 | 10.4 |  |  | 0.68838
11:30 | 4133 | 57 | 261.9 | 10.4 |  |  | 0.68838
11:30 | 4134 | 59 | 261.7 | 10.4 |  |  | 0.68864
11:30 | 4141 | 59 | 261.7 | 10.4 |  |  | 0.68864
11:30 | 4141 | 60 | 261.9 | 10.4 |  |  | 0.68838
11:30 | 4142 | 63 | 261.9 | 10.5 |  |  | 0.68838
11:30 | 4143 | 69 | 261.7 | 10.5 |  |  | 0.68864
11:30 | 4135 | 69 | 261.7 | 10.5 |  |  | 0.68864
11:30 | 4128 | 67 | 261.8 | 10.5 |  |  | 0.68851
11:30 | 4123 | 67 | 261.9 | 10.5 |  |  | 0.68838
11:30 | 4116 | 62 | 261.9 | 10.5 |  |  | 0.68838
11:30 | 4116 | 61 | 261.9 | 10.4 |  |  | 0.68838
11:30 | 4119 | 59 | 261.9 | 10.4 |  |  | 0.68838
11:30 | 4119 | 57 | 262.3 | 10.4 |  |  | 0.68786
11:30 | 4123 | 59 | 262.3 | 10.4 |  |  | 0.68786
11:30 | 4124 | 63 | 262.4 | 10.4 |  |  | 0.68774
11:30 | 4122 | 63 | 262.5 | 10.4 |  |  | 0.68761
11:30 | 4120 | 63 | 262.5 | 10.4 |  |  | 0.68761
11:30 | 4114 | 63 | 262.5 | 10.4 |  |  | 0.68761
11:30 | 4104 | 64 | 262.4 | 10.4 |  |  | 0.68774
11:30 | 4103 | 64 | 262.4 | 10.4 |  |  | 0.68774
11:30 | 4093 | 62 | 262.4 | 10.4 |  |  | 0.68774
11:30 | 4093 | 60 | 262.3 | 10.4 |  |  | 0.68786
11:30 | 4095 | 57 | 262.3 | 10.4 |  |  | 0.68786
11:30 | 4095 | 51 | 262.1 | 10.4 |  |  | 0.68812
11:30 | 4096 | 51 | 262.1 | 10.4 |  |  | 0.68812
11:30 | 4097 | 45 | 261.9 | 10.4 |  |  | 0.68838

## P6
| Port | 6
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current
| Pa | Pa | Deg C | mA
Averages | 4056.0508 | 33.6813 | 260.9296 | 10.3448 | [11 empty] | 9.1999 |  | 9.3171
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current |  |  |  |  | a | b | n | h | xi | f(xi) | Aj
| Pa. | Pa | Deg C | mA |  | 10.1897 |  |  | 0 | 1 | 100 | 0.01 | 0 | 12.6127
[6 empty] | vel | dens | [5 empty] | 0.01 | 12.6127 | 0.12613 |  | 0.2507
11:32 | 4045 | 55 | 259.3 | 10.4 | 1 | 12.6127 | 0.69174 | 12.0691 |  |  |  |  | 0.02 | 12.1454 | 0.12379
11:32 | 4044 | 55 | 259.3 | 10.4 | 2 | 12.6127 | 0.69174 | 12.0974 |  |  |  |  | 0.03 | 11.7839 | 0.11965 |  | 0.23729
11:32 | 4042 | 51 | 259.3 | 10.4 | 3 | 12.1454 | 0.69174 | 12.1249 |  |  |  |  | 0.04 | 11.906 | 0.11845
11:32 | 4042 | 48 | 259.4 | 10.4 | 4 | 11.7839 | 0.69161 | 12.1516 |  |  |  |  | 0.05 | 12.1466 | 0.12026 |  | 0.24213
11:32 | 4047 | 49 | 259.4 | 10.4 | 5 | 11.906 | 0.69161 | 12.1775 |  |  |  |  | 0.06 | 12.1466 | 0.12147
11:32 | 4047 | 51 | 259.4 | 10.4 | 6 | 12.1466 | 0.69161 | 12.2026 |  |  |  |  | 0.07 | 11.1533 | 0.1165 |  | 0.22638
11:32 | 4047 | 51 | 259.4 | 10.3 | 7 | 12.1466 | 0.69161 | 12.2269 |  |  |  |  | 0.08 | 11.1543 | 0.11154
11:32 | 4046 | 43 | 259.4 | 10.3 | 8 | 11.1533 | 0.69161 | 12.2505 |  |  |  |  | 0.09 | 11.5369 | 0.11346 |  | 0.22946
11:32 | 4044 | 43 | 259.5 | 10.4 | 9 | 11.1543 | 0.69148 | 12.2732 |  |  |  |  | 0.1 | 11.5358 | 0.11536
11:32 | 4041 | 46 | 259.5 | 10.4 | 10 | 11.5369 | 0.69148 | 12.2951 |  |  |  |  | 0.11 | 11.785 | 0.1166 |  | 0.23568
11:32 | 4041 | 46 | 259.4 | 10.4 | 11 | 11.5358 | 0.69161 | 12.3163 |  |  |  |  | 0.12 | 12.028 | 0.11907
11:32 | 4032 | 48 | 259.5 | 10.4 | 12 | 11.785 | 0.69148 | 12.3367 |  |  |  |  | 0.13 | 11.785 | 0.11907 |  | 0.23567
11:32 | 4032 | 50 | 259.5 | 10.4 | 13 | 12.028 | 0.69148 | 12.3563 |  |  |  |  | 0.14 | 11.5336 | 0.11659
11:32 | 4032 | 48 | 259.5 | 10.4 | 14 | 11.785 | 0.69148 | 12.3751 |  |  |  |  | 0.15 | 11.5336 | 0.11534 |  | 0.23109
11:32 | 4031 | 46 | 259.2 | 10.4 | 15 | 11.5336 | 0.69187 | 12.3932 |  |  |  |  | 0.16 | 11.6594 | 0.11597
11:32 | 4048 | 46 | 259.2 | 10.4 | 16 | 11.5336 | 0.69187 | 12.4104 |  |  |  |  | 0.17 | 11.6616 | 0.11661 |  | 0.23404
11:32 | 4064 | 47 | 259.3 | 10.4 | 17 | 11.6594 | 0.69174 | 12.427 |  |  |  |  | 0.18 | 11.906 | 0.11784
11:32 | 4069 | 47 | 259.5 | 10.4 | 18 | 11.6616 | 0.69148 | 12.4427 |  |  |  |  | 0.19 | 12.0246 | 0.11965 |  | 0.2401
11:32 | 4077 | 49 | 259.4 | 10.4 | 19 | 11.906 | 0.69161 | 12.4577 |  |  |  |  | 0.2 | 12.0246 | 0.12025
11:32 | 4078 | 50 | 259.2 | 10.4 | 20 | 12.0246 | 0.69187 | 12.4719 |  |  |  |  | 0.21 | 12.0235 | 0.12024 |  | 0.24166
11:32 | 4088 | 50 | 259.2 | 10.4 | 21 | 12.0246 | 0.69187 | 12.4854 |  |  |  |  | 0.22 | 12.379 | 0.12201
11:32 | 4088 | 50 | 259.1 | 10.4 | 22 | 12.0235 | 0.692 | 12.4981 |  |  |  |  | 0.23 | 13.2804 | 0.1283 |  | 0.2626
11:32 | 4091 | 53 | 259.1 | 10.4 | 23 | 12.379 | 0.692 | 12.5101 |  |  |  |  | 0.24 | 13.2791 | 0.1328
11:32 | 4092 | 61 | 259.1 | 10.4 | 24 | 13.2804 | 0.692 | 12.5213 |  |  |  |  | 0.25 | 14.3277 | 0.13803 |  | 0.28306
11:32 | 4092 | 61 | 259 | 10.4 | 25 | 13.2791 | 0.69213 | 12.5318 |  |  |  |  | 0.26 | 14.329 | 0.14328
11:32 | 4092 | 71 | 259.1 | 10.4 | 26 | 14.3277 | 0.692 | 12.5415 |  |  |  |  | 0.27 | 14.0243 | 0.14177 |  | 0.28116
11:32 | 4094 | 71 | 259.2 | 10.4 | 27 | 14.329 | 0.69187 | 12.5505 |  |  |  |  | 0.28 | 13.9208 | 0.13973
11:32 | 4096 | 68 | 259.3 | 10.4 | 28 | 14.0243 | 0.69174 | 12.5587 |  |  |  |  | 0.29 | 14.0243 | 0.13973 |  | 0.28014
11:32 | 4096 | 67 | 259.3 | 10.4 | 29 | 13.9208 | 0.69174 | 12.5662 |  |  |  |  | 0.3 | 14.0243 | 0.14024
11:32 | 4095 | 68 | 259.3 | 10.4 | 30 | 14.0243 | 0.69174 | 12.573 |  |  |  |  | 0.31 | 13.7115 | 0.13868 |  | 0.27199
11:32 | 4095 | 68 | 259.3 | 10.4 | 31 | 14.0243 | 0.69174 | 12.5791 |  |  |  |  | 0.32 | 12.7281 | 0.1322
11:32 | 4097 | 65 | 259.3 | 10.4 | 32 | 13.7115 | 0.69174 | 12.5844 |  |  |  |  | 0.33 | 12.7293 | 0.12729 |  | 0.25497
11:32 | 4098 | 56 | 259.4 | 10.4 | 33 | 12.7281 | 0.69161 | 12.589 |  |  |  |  | 0.34 | 12.8448 | 0.12787
11:32 | 4103 | 56 | 259.5 | 10.4 | 34 | 12.7293 | 0.69148 | 12.5929 |  |  |  |  | 0.35 | 12.846 | 0.12845 |  | 0.25729
11:32 | 4107 | 57 | 259.7 | 10.4 | 35 | 12.8448 | 0.69122 | 12.596 |  |  |  |  | 0.36 | 12.9582 | 0.12902
11:32 | 4107 | 57 | 259.8 | 10.4 | 36 | 12.846 | 0.69109 | 12.5984 |  |  |  |  | 0.37 | 13.0695 | 0.13014 |  | 0.26027
11:32 | 4106 | 58 | 259.8 | 10.4 | 37 | 12.9582 | 0.69109 | 12.6001 |  |  |  |  | 0.38 | 12.846 | 0.12958
11:32 | 4107 | 59 | 259.8 | 10.4 | 38 | 13.0695 | 0.69109 | 12.6011 |  |  |  |  | 0.39 | 12.7328 | 0.12789 |  | 0.25503
11:32 | 4112 | 57 | 259.8 | 10.4 | 39 | 12.846 | 0.69109 | 12.6014 |  |  |  |  | 0.4 | 12.7328 | 0.12733
11:32 | 4112 | 56 | 259.8 | 10.4 | 40 | 12.7328 | 0.69109 | 12.601 |  |  |  |  | 0.41 | 12.6198 | 0.12676 |  | 0.25278
11:32 | 4131 | 56 | 259.8 | 10.4 | 41 | 12.7328 | 0.69109 | 12.5999 |  |  |  |  | 0.42 | 12.621 | 0.1262
11:32 | 4137 | 55 | 259.9 | 10.4 | 42 | 12.6198 | 0.69096 | 12.5981 |  |  |  |  | 0.43 | 13.4001 | 0.13011 |  | 0.26541
11:32 | 4138 | 55 | 260 | 10.4 | 43 | 12.621 | 0.69083 | 12.5956 |  |  |  |  | 0.44 | 13.4001 | 0.134
11:32 | 4139 | 62 | 260 | 10.4 | 44 | 13.4001 | 0.69083 | 12.5923 |  |  |  |  | 0.45 | 13.4001 | 0.134 |  | 0.268
11:32 | 4135 | 62 | 260 | 10.4 | 45 | 13.4001 | 0.69083 | 12.5884 |  |  |  |  | 0.46 | 13.4001 | 0.134
11:32 | 4127 | 62 | 260 | 10.4 | 46 | 13.4001 | 0.69083 | 12.5838 |  |  |  |  | 0.47 | 13.4001 | 0.134 |  | 0.268
11:32 | 4126 | 62 | 260 | 10.4 | 47 | 13.4001 | 0.69083 | 12.5785 |  |  |  |  | 0.48 | 13.4001 | 0.134
11:32 | 4109 | 62 | 260 | 10.4 | 48 | 13.4001 | 0.69083 | 12.5726 |  |  |  |  | 0.49 | 13.4001 | 0.134 |  | 0.26801
11:32 | 4109 | 62 | 260 | 10.4 | 49 | 13.4001 | 0.69083 | 12.5659 |  |  |  |  | 0.5 | 13.4014 | 0.13401
11:32 | 4091 | 62 | 260 | 10.4 | 50 | 13.4001 | 0.69083 | 12.5585 |  |  |  |  | 0.51 | 13.4014 | 0.13401 |  | 0.26803
11:32 | 4085 | 62 | 260.1 | 10.4 | 51 | 13.4014 | 0.6907 | 12.5505 |  |  |  |  | 0.52 | 13.4026 | 0.13402
11:32 | 4085 | 62 | 260.1 | 10.4 | 52 | 13.4014 | 0.6907 | 12.5418 |  |  |  |  | 0.53 | 13.4026 | 0.13403 |  | 0.26805
11:32 | 4084 | 62 | 260.2 | 10.4 | 53 | 13.4026 | 0.69057 | 12.5325 |  |  |  |  | 0.54 | 13.4026 | 0.13403
11:32 | 4080 | 62 | 260.2 | 10.3 | 54 | 13.4026 | 0.69057 | 12.5224 |  |  |  |  | 0.55 | 13.4026 | 0.13403 |  | 0.26696
11:32 | 4069 | 62 | 260.2 | 10.3 | 55 | 13.4026 | 0.69057 | 12.5117 |  |  |  |  | 0.56 | 13.0744 | 0.13238
11:32 | 4068 | 62 | 260.2 | 10.4 | 56 | 13.4026 | 0.69057 | 12.5003 |  |  |  |  | 0.57 | 12.7352 | 0.12905 |  | 0.25621
11:32 | 4061 | 59 | 260.2 | 10.4 | 57 | 13.0744 | 0.69057 | 12.4883 |  |  |  |  | 0.58 | 12.8484 | 0.12792
11:32 | 4061 | 56 | 260 | 10.4 | 58 | 12.7352 | 0.69083 | 12.4756 |  |  |  |  | 0.59 | 12.8496 | 0.12849 |  | 0.25699
11:32 | 4068 | 57 | 260 | 10.4 | 59 | 12.8484 | 0.69083 | 12.4622 |  |  |  |  | 0.6 | 12.8496 | 0.1285
11:32 | 4072 | 57 | 260.1 | 10.4 | 60 | 12.8496 | 0.6907 | 12.4482 |  |  |  |  | 0.61 | 12.8496 | 0.1285 |  | 0.25699
11:32 | 4067 | 57 | 260.1 | 10.4 | 61 | 12.8496 | 0.6907 | 12.4335 |  |  |  |  | 0.62 | 12.8496 | 0.1285
11:32 | 4063 | 57 | 260.1 | 10.4 | 62 | 12.8496 | 0.6907 | 12.4182 |  |  |  |  | 0.63 | 11.6682 | 0.12259 |  | 0.23561
11:32 | 4060 | 57 | 260.1 | 10.3 | 63 | 12.8496 | 0.6907 | 12.4023 |  |  |  |  | 0.64 | 11.1606 | 0.11414
11:32 | 4052 | 47 | 260.1 | 10.3 | 64 | 11.6682 | 0.6907 | 12.3857 |  |  |  |  | 0.65 | 10.7642 | 0.10962 |  | 0.2157
11:32 | 4053 | 43 | 260.1 | 10.3 | 65 | 11.1606 | 0.6907 | 12.3684 |  |  |  |  | 0.66 | 10.4917 | 0.10628
11:32 | 4059 | 40 | 260.1 | 10.3 | 66 | 10.7642 | 0.6907 | 12.3505 |  |  |  |  | 0.67 | 10.4917 | 0.10492 |  | 0.21163
11:32 | 4059 | 38 | 260.1 | 10.3 | 67 | 10.4917 | 0.6907 | 12.332 |  |  |  |  | 0.68 | 11.0311 | 0.10761
11:32 | 4053 | 38 | 260.1 | 10.3 | 68 | 10.4917 | 0.6907 | 12.3128 |  |  |  |  | 0.69 | 11.0311 | 0.11031 |  | 0.22106
11:32 | 4050 | 42 | 260.2 | 10.3 | 69 | 11.0311 | 0.69057 | 12.293 |  |  |  |  | 0.7 | 11.1627 | 0.11097
11:32 | 4040 | 42 | 260.2 | 10.3 | 70 | 11.0311 | 0.69057 | 12.2726 |  |  |  |  | 0.71 | 11.1627 | 0.11163 |  | 0.22368
11:32 | 4031 | 43 | 260.3 | 10.3 | 71 | 11.1627 | 0.69044 | 12.2516 |  |  |  |  | 0.72 | 11.2918 | 0.11227
11:32 | 4029 | 43 | 260.3 | 10.4 | 72 | 11.1627 | 0.69044 | 12.2299 |  |  |  |  | 0.73 | 11.2918 | 0.11292 |  | 0.22584
11:32 | 4024 | 44 | 260.3 | 10.4 | 73 | 11.2918 | 0.69044 | 12.2076 |  |  |  |  | 0.74 | 11.2918 | 0.11292
11:32 | 4024 | 44 | 260.3 | 10.3 | 74 | 11.2918 | 0.69044 | 12.1847 |  |  |  |  | 0.75 | 11.4183 | 0.11355 |  | 0.22752
11:32 | 4017 | 44 | 260.3 | 10.3 | 75 | 11.2918 | 0.69044 | 12.1612 |  |  |  |  | 0.76 | 11.2907 | 0.11354
11:32 | 4017 | 45 | 260.2 | 10.3 | 76 | 11.4183 | 0.69057 | 12.137 |  |  |  |  | 0.77 | 11.0321 | 0.11161 |  | 0.2215
11:32 | 4027 | 44 | 260.2 | 10.3 | 77 | 11.2907 | 0.69057 | 12.1123 |  |  |  |  | 0.78 | 11.0321 | 0.11032
11:32 | 4033 | 42 | 260.3 | 10.3 | 78 | 11.0321 | 0.69044 | 12.0869 |  |  |  |  | 0.79 | 11.4215 | 0.11227 |  | 0.22714
11:32 | 4036 | 42 | 260.3 | 10.3 | 79 | 11.0321 | 0.69044 | 12.061 |  |  |  |  | 0.8 | 11.4236 | 0.11423
11:32 | 4039 | 45 | 260.5 | 10.3 | 80 | 11.4215 | 0.69018 | 12.0344 |  |  |  |  | 0.81 | 11.2949 | 0.11359 |  | 0.22589
11:32 | 4039 | 45 | 260.7 | 10.3 | 81 | 11.4236 | 0.68993 | 12.0072 |  |  |  |  | 0.82 | 11.1648 | 0.1123
11:32 | 4041 | 44 | 260.6 | 10.3 | 82 | 11.2949 | 0.69006 | 11.9795 |  |  |  |  | 0.83 | 11.1648 | 0.11165 |  | 0.2233
11:32 | 4041 | 43 | 260.5 | 10.3 | 83 | 11.1648 | 0.69018 | 11.9511 |  |  |  |  | 0.84 | 11.1648 | 0.11165
11:32 | 4043 | 43 | 260.5 | 10.3 | 84 | 11.1648 | 0.69018 | 11.9222 |  |  |  |  | 0.85 | 11.2939 | 0.11229 |  | 0.22629
11:32 | 4043 | 43 | 260.5 | 10.3 | 85 | 11.1648 | 0.69018 | 11.8926 |  |  |  |  | 0.86 | 11.5477 | 0.11421
11:32 | 4045 | 44 | 260.5 | 10.3 | 86 | 11.2939 | 0.69018 | 11.8625 |  |  |  |  | 0.87 | 11.5477 | 0.11548 |  | 0.23096
11:32 | 4046 | 46 | 260.5 | 10.3 | 87 | 11.5477 | 0.69018 | 11.8318 |  |  |  |  | 0.88 | 11.5488 | 0.11548
11:32 | 4047 | 46 | 260.5 | 10.3 | 88 | 11.5477 | 0.69018 | 11.8005 |  |  |  |  | 0.89 | 11.5499 | 0.11549 |  | 0.23057
11:32 | 4048 | 46 | 260.6 | 10.3 | 89 | 11.5488 | 0.69006 | 11.7686 |  |  |  |  | 0.9 | 11.4236 | 0.11487
11:32 | 4049 | 46 | 260.7 | 10.3 | 90 | 11.5499 | 0.68993 | 11.7361 |  |  |  |  | 0.91 | 11.4215 | 0.11423 |  | 0.22715
11:32 | 4050 | 45 | 260.7 | 10.3 | 91 | 11.4236 | 0.68993 | 11.7031 |  |  |  |  | 0.92 | 11.0342 | 0.11228
11:32 | 4050 | 45 | 260.5 | 10.3 | 92 | 11.4215 | 0.69018 | 11.6695 |  |  |  |  | 0.93 | 10.7683 | 0.10901 |  | 0.21625
11:32 | 4047 | 42 | 260.5 | 10.3 | 93 | 11.0342 | 0.69018 | 11.6354 |  |  |  |  | 0.94 | 10.7683 | 0.10768
11:32 | 4047 | 40 | 260.5 | 10.3 | 94 | 10.7683 | 0.69018 | 11.6006 |  |  |  |  | 0.95 | 10.9021 | 0.10835 |  | 0.2176
11:32 | 4044 | 40 | 260.5 | 10.3 | 95 | 10.7683 | 0.69018 | 11.5653 |  |  |  |  | 0.96 | 10.9021 | 0.10902
11:32 | 4042 | 41 | 260.5 | 10.3 | 96 | 10.9021 | 0.69018 | 11.5295 |  |  |  |  | 0.97 | 11.5477 | 0.11225 |  | 0.2288
11:32 | 4041 | 41 | 260.5 | 10.3 | 97 | 10.9021 | 0.69018 | 11.4931 |  |  |  |  | 0.98 | 11.5477 | 0.11548
11:32 | 4040 | 46 | 260.5 | 10.3 | 98 | 11.5477 | 0.69018 | 11.4561 |  |  |  |  | 0.99 | 11.6725 | 0.1161 |  | 0.23345
11:32 | 4039 | 46 | 260.5 | 10.3 | 99 | 11.5477 | 0.69018 | 11.4186 |  |  |  |  | 1 | 11.7961 | 0.11734
11:32 | 4038 | 47 | 260.5 | 10.3 | 100 | 11.6725 | 0.69018 | 11.3805 |  |  |  |  | 0 | 11.4215 | -11.6088 |  | -11.3265
11:32 | 4038 | 48 | 260.5 | 10.3 | 101 | 11.7961 | 0.69018 | 11.3419 |  |  |  |  | 0.01 | 11.1637 | 0.11293
11:32 | 4044 | 45 | 260.5 | 10.3 | 102 | 11.4215 | 0.69018 | 11.3027 |  |  |  |  | 0.02 | 11.2928 | 0.11228 |  | 0.22871
11:32 | 4044 | 43 | 260.4 | 10.3 | 103 | 11.1637 | 0.69031 | 11.263 |  |  |  |  | 0.03 | 12.2766 | 0.11785
11:32 | 4050 | 44 | 260.4 | 10.3 | 104 | 11.2928 | 0.69031 | 11.2228 |  |  |  |  | 0.04 | 12.2766 | 0.12277 |  | 0.24351
11:32 | 4055 | 52 | 260.4 | 10.3 | 105 | 12.2766 | 0.69031 | 11.182 |  |  |  |  | 0.05 | 11.6714 | 0.11974
11:33 | 4063 | 52 | 260.4 | 10.3 | 106 | 12.2766 | 0.69031 | 11.1406 |  |  |  |  | 0.06 | 11.6714 | 0.11671 |  | 0.23217
11:33 | 4070 | 47 | 260.4 | 10.3 | 107 | 11.6714 | 0.69031 | 11.0988 |  |  |  |  | 0.07 | 11.2939 | 0.11483
11:33 | 4071 | 47 | 260.4 | 10.3 | 108 | 11.6714 | 0.69031 | 11.0564 |  |  |  |  | 0.08 | 11.0363 | 0.11165 |  | 0.22114
11:33 | 4075 | 44 | 260.5 | 10.3 | 109 | 11.2939 | 0.69018 | 11.0135 |  |  |  |  | 0.09 | 10.9041 | 0.1097
11:33 | 4075 | 42 | 260.7 | 10.3 | 110 | 11.0363 | 0.68993 | 10.9701 |  |  |  |  | 0.1 | 10.7693 | 0.10837 |  | 0.21584
11:33 | 4064 | 41 | 260.7 | 10.3 | 111 | 10.9041 | 0.68993 | 10.9261 |  |  |  |  | 0.11 | 10.7693 | 0.10769
11:33 | 4064 | 40 | 260.6 | 10.3 | 112 | 10.7693 | 0.69006 | 10.8816 |  |  |  |  | 0.12 | 10.2176 | 0.10493 |  | 0.20619
11:33 | 4063 | 40 | 260.6 | 10.3 | 113 | 10.7693 | 0.69006 | 10.8366 |  |  |  |  | 0.13 | 10.2186 | 0.10218
11:33 | 4062 | 36 | 260.7 | 10.3 | 114 | 10.2176 | 0.68993 | 10.7911 |  |  |  |  | 0.14 | 9.7835 | 0.10001 |  | 0.19712
11:33 | 4063 | 36 | 260.8 | 10.4 | 115 | 10.2186 | 0.6898 | 10.7451 |  |  |  |  | 0.15 | 9.7844 | 0.09784
11:33 | 4064 | 33 | 260.8 | 10.4 | 116 | 9.7835 | 0.6898 | 10.6986 |  |  |  |  | 0.16 | 10.3605 | 0.10072 |  | 0.20666
11:33 | 4062 | 33 | 260.9 | 10.3 | 117 | 9.7844 | 0.68967 | 10.6516 |  |  |  |  | 0.17 | 10.7723 | 0.10566
11:33 | 4045 | 37 | 260.9 | 10.3 | 118 | 10.3605 | 0.68967 | 10.604 |  |  |  |  | 0.18 | 10.9061 | 0.10839 |  | 0.21767
11:33 | 4044 | 40 | 260.9 | 10.3 | 119 | 10.7723 | 0.68967 | 10.556 |  |  |  |  | 0.19 | 10.9051 | 0.10906
11:33 | 4018 | 41 | 260.9 | 10.3 | 120 | 10.9061 | 0.68967 | 10.5074 |  |  |  |  | 0.2 | 10.9051 | 0.10905 |  | 0.21436
11:33 | 4018 | 41 | 260.8 | 10.3 | 121 | 10.9051 | 0.6898 | 10.4584 |  |  |  |  | 0.21 | 9.7835 | 0.10344
11:33 | 4008 | 41 | 260.8 | 10.3 | 122 | 10.9051 | 0.6898 | 10.4089 |  |  |  |  | 0.22 | 9.7835 | 0.097835 |  | 0.19759
11:33 | 3999 | 33 | 260.8 | 10.3 | 123 | 9.7835 | 0.6898 | 10.3589 |  |  |  |  | 0.23 | 10.3595 | 0.10072
11:33 | 3999 | 33 | 260.8 | 10.3 | 124 | 9.7835 | 0.6898 | 10.3084 |  |  |  |  | 0.24 | 10.3595 | 0.1036 |  | 0.20856
11:33 | 3999 | 37 | 260.8 | 10.3 | 125 | 10.3595 | 0.6898 | 10.2574 |  |  |  |  | 0.25 | 10.7713 | 0.10565
11:33 | 4000 | 37 | 260.8 | 10.3 | 126 | 10.3595 | 0.6898 | 10.2059 |  |  |  |  | 0.26 | 11.0373 | 0.10904 |  | 0.21942
11:33 | 4011 | 40 | 260.8 | 10.3 | 127 | 10.7713 | 0.6898 | 10.154 |  |  |  |  | 0.27 | 10.9051 | 0.10971
11:33 | 4011 | 42 | 260.8 | 10.3 | 128 | 11.0373 | 0.6898 | 10.1015 |  |  |  |  | 0.28 | 10.9061 | 0.10906 |  | 0.21812
11:33 | 4010 | 41 | 260.8 | 10.3 | 129 | 10.9051 | 0.6898 | 10.0486 |  |  |  |  | 0.29 | 10.9061 | 0.10906
11:33 | 4010 | 41 | 260.9 | 10.3 | 130 | 10.9061 | 0.68967 | 9.9953 |  |  |  |  | 0.3 | 10.9041 | 0.10905 |  | 0.21809
11:33 | 4010 | 41 | 260.9 | 10.3 | 131 | 10.9061 | 0.68967 | 9.9414 |  |  |  |  | 0.31 | 10.9031 | 0.10904
11:33 | 4010 | 41 | 260.7 | 10.3 | 132 | 10.9041 | 0.68993 | 9.8871 |  |  |  |  | 0.32 | 10.6348 | 0.10769 |  | 0.2136
11:33 | 4014 | 41 | 260.6 | 10.3 | 133 | 10.9031 | 0.69006 | 9.8323 |  |  |  |  | 0.33 | 10.6368 | 0.10636
11:33 | 4018 | 39 | 260.7 | 10.3 | 134 | 10.6348 | 0.68993 | 9.7771 |  |  |  |  | 0.34 | 10.3605 | 0.10499 |  | 0.20766
11:33 | 4019 | 39 | 260.9 | 10.3 | 135 | 10.6368 | 0.68967 | 9.7214 |  |  |  |  | 0.35 | 10.2186 | 0.1029
11:33 | 4031 | 37 | 260.9 | 10.3 | 136 | 10.3605 | 0.68967 | 9.6653 |  |  |  |  | 0.36 | 9.9307 | 0.10075 |  | 0.19859
11:33 | 4031 | 36 | 260.8 | 10.3 | 137 | 10.2186 | 0.6898 | 9.6087 |  |  |  |  | 0.37 | 9.636 | 0.097833
11:33 | 4040 | 34 | 260.8 | 10.3 | 138 | 9.9307 | 0.6898 | 9.5516 |  |  |  |  | 0.38 | 9.636 | 0.09636 |  | 0.1937
11:33 | 4040 | 32 | 261 | 10.3 | 139 | 9.636 | 0.68954 | 9.4941 |  |  |  |  | 0.39 | 9.9316 | 0.097838
11:33 | 4045 | 32 | 261 | 10.3 | 140 | 9.636 | 0.68954 | 9.4362 |  |  |  |  | 0.4 | 9.9307 | 0.099311 |  | 0.19661
11:33 | 4048 | 34 | 260.9 | 10.3 | 141 | 9.9316 | 0.68967 | 9.3778 |  |  |  |  | 0.41 | 9.3291 | 0.096299
11:33 | 4045 | 34 | 260.8 | 10.3 | 142 | 9.9307 | 0.6898 | 9.3189 |  |  |  |  | 0.42 | 9.1732 | 0.092511 |  | 0.18345
11:33 | 4042 | 30 | 260.9 | 10.3 | 143 | 9.3291 | 0.68967 | 9.2597 |  |  |  |  | 0.43 | 9.0136 | 0.090934
11:33 | 4041 | 29 | 261 | 10.3 | 144 | 9.1732 | 0.68954 | 9.1999 |  |  |  |  | 0.44 | 9.0136 | 0.090136 |  | 0.18133
11:33 | 4034 | 28 | 261 | 10.3 | 145 | 9.0136 | 0.68954 | 9.1398 |  |  |  |  | 0.45 | 9.33 | 0.091718
11:33 | 4034 | 28 | 261 | 10.4 | 146 | 9.0136 | 0.68954 | 9.0792 |  |  |  |  | 0.46 | 9.6378 | 0.094839 |  | 0.19173
11:33 | 4029 | 30 | 261 | 10.4 | 147 | 9.33 | 0.68954 | 9.0182 |  |  |  |  | 0.47 | 9.6378 | 0.096378
11:33 | 4029 | 32 | 261.2 | 10.4 | 148 | 9.6378 | 0.68928 | 8.9568 |  |  |  |  | 0.48 | 9.3317 | 0.094847 |  | 0.18765
11:33 | 4029 | 32 | 261.2 | 10.4 | 149 | 9.6378 | 0.68928 | 8.895 |  |  |  |  | 0.49 | 9.3308 | 0.093313
11:33 | 4029 | 30 | 261.2 | 10.4 | 150 | 9.3317 | 0.68928 | 8.8327 |  |  |  |  | 0.5 | 8.8528 | 0.090918 |  | 0.17865
11:33 | 4033 | 30 | 261.1 | 10.4 | 151 | 9.3308 | 0.68941 | 8.77 |  |  |  |  | 0.51 | 8.8528 | 0.088528
11:33 | 4037 | 27 | 261.2 | 10.4 | 152 | 8.8528 | 0.68928 | 8.7069 |  |  |  |  | 0.52 | 8.6874 | 0.087701 |  | 0.17374
11:33 | 4038 | 27 | 261.2 | 10.4 | 153 | 8.8528 | 0.68928 | 8.6434 |  |  |  |  | 0.53 | 8.5187 | 0.08603
11:33 | 4046 | 26 | 261.2 | 10.4 | 154 | 8.6874 | 0.68928 | 8.5795 |  |  |  |  | 0.54 | 8.6874 | 0.08603 |  | 0.17374
11:33 | 4046 | 25 | 261.2 | 10.4 | 155 | 8.5187 | 0.68928 | 8.5152 |  |  |  |  | 0.55 | 8.8545 | 0.087709
11:33 | 4052 | 26 | 261.2 | 10.4 | 156 | 8.6874 | 0.68928 | 8.4504 |  |  |  |  | 0.56 | 9.017 | 0.089357 |  | 0.18136
11:33 | 4053 | 27 | 261.4 | 10.4 | 157 | 8.8545 | 0.68902 | 8.3853 |  |  |  |  | 0.57 | 9.4869 | 0.092519
11:33 | 4053 | 28 | 261.4 | 10.4 | 158 | 9.017 | 0.68902 | 8.3198 |  |  |  |  | 0.58 | 9.4869 | 0.094869 |  | 0.18651
11:33 | 4054 | 31 | 261.3 | 10.4 | 159 | 9.4869 | 0.68915 | 8.2539 |  |  |  |  | 0.59 | 8.5194 | 0.090032
11:33 | 4055 | 31 | 261.3 | 10.4 | 160 | 9.4869 | 0.68915 | 8.1875 |  |  |  |  | 0.6 | 8.3465 | 0.08433 |  | 0.16808
11:33 | 4055 | 25 | 261.3 | 10.4 | 161 | 8.5194 | 0.68915 | 8.1208 |  |  |  |  | 0.61 | 8.5187 | 0.084326
11:33 | 4057 | 24 | 261.2 | 10.4 | 162 | 8.3465 | 0.68928 | 8.0537 |  |  |  |  | 0.62 | 8.5187 | 0.085187 |  | 0.17037
11:33 | 4078 | 25 | 261.2 | 10.4 | 163 | 8.5187 | 0.68928 | 7.9862 |  |  |  |  | 0.63 | 8.5187 | 0.085187
11:33 | 4078 | 25 | 261.2 | 10.4 | 164 | 8.5187 | 0.68928 | 7.9184 |  |  |  |  | 0.64 | 8.5187 | 0.085187 |  | 0.17037
11:33 | 4071 | 25 | 261.2 | 10.4 | 165 | 8.5187 | 0.68928 | 7.8501 |  |  |  |  | 0.65 | 8.5187 | 0.085187
11:33 | 4070 | 25 | 261.2 | 10.4 | 166 | 8.5187 | 0.68928 | 7.7815 |  |  |  |  | 0.66 | 7.992 | 0.082553 |  | 0.16159
11:33 | 4062 | 25 | 261.2 | 10.4 | 167 | 8.5187 | 0.68928 | 7.7125 |  |  |  |  | 0.67 | 7.992 | 0.07992
11:33 | 4054 | 22 | 261.3 | 10.4 | 168 | 7.992 | 0.68915 | 7.6431 |  |  |  |  | 0.68 | 7.0253 | 0.075086 |  | 0.14373
11:33 | 4047 | 22 | 261.3 | 10.4 | 169 | 7.992 | 0.68915 | 7.5734 |  |  |  |  | 0.69 | 7.0247 | 0.07025
11:33 | 4037 | 17 | 261.3 | 10.4 | 170 | 7.0253 | 0.68915 | 7.5033 |  |  |  |  | 0.7 | 6.1429 | 0.065838 |  | 0.12328
11:33 | 4036 | 17 | 261.2 | 10.4 | 171 | 7.0247 | 0.68928 | 7.4328 |  |  |  |  | 0.71 | 5.3877 | 0.057653
11:33 | 4025 | 13 | 261.2 | 10.4 | 172 | 6.1429 | 0.68928 | 7.3619 |  |  |  |  | 0.72 | 5.3877 | 0.053877 |  | 0.10775
11:33 | 4025 | 10 | 261.2 | 10.4 | 173 | 5.3877 | 0.68928 | 7.2908 |  |  |  |  | 0.73 | 5.3877 | 0.053877
11:33 | 4033 | 10 | 261.2 | 10.4 | 174 | 5.3877 | 0.68928 | 7.2192 |  |  |  |  | 0.74 | 5.3877 | 0.053877 |  | 0.11027
11:33 | 4034 | 10 | 261.2 | 10.4 | 175 | 5.3877 | 0.68928 | 7.1473 |  |  |  |  | 0.75 | 6.1423 | 0.05765
11:33 | 4036 | 10 | 261.2 | 10.4 | 176 | 5.3877 | 0.68928 | 7.075 |  |  |  |  | 0.76 | 6.1417 | 0.06142 |  | 0.1194
11:33 | 4037 | 13 | 261.1 | 10.4 | 177 | 6.1423 | 0.68941 | 7.0024 |  |  |  |  | 0.77 | 5.1102 | 0.05626
11:33 | 4043 | 13 | 261 | 10.4 | 178 | 6.1417 | 0.68954 | 6.9295 |  |  |  |  | 0.78 | 4.8184 | 0.049643 |  | 0.099237
11:33 | 4051 | 9 | 261 | 10.4 | 179 | 5.1102 | 0.68954 | 6.8562 |  |  |  |  | 0.79 | 5.3872 | 0.051028
11:33 | 4052 | 8 | 261.1 | 10.4 | 180 | 4.8184 | 0.68941 | 6.7825 |  |  |  |  | 0.8 | 5.6506 | 0.055189 |  | 0.11213
11:33 | 4069 | 10 | 261.1 | 10.4 | 181 | 5.3872 | 0.68941 | 6.7085 |  |  |  |  | 0.81 | 5.6506 | 0.056506
11:33 | 4069 | 11 | 261.2 | 10.4 | 182 | 5.6506 | 0.68928 | 6.6342 |  |  |  |  | 0.82 | 5.9024 | 0.057765 |  | 0.11721
11:33 | 4073 | 11 | 261.2 | 10.4 | 183 | 5.6506 | 0.68928 | 6.5596 |  |  |  |  | 0.83 | 5.903 | 0.059027
11:33 | 4074 | 12 | 261.3 | 10.4 | 184 | 5.9024 | 0.68915 | 6.4846 |  |  |  |  | 0.84 | 4.1741 | 0.050385 |  | 0.089244
11:33 | 4084 | 12 | 261.4 | 10.4 | 185 | 5.903 | 0.68902 | 6.4093 |  |  |  |  | 0.85 | 4.1741 | 0.041741
11:33 | 4094 | 6 | 261.4 | 10.4 | 186 | 4.1741 | 0.68902 | 6.3336 |  |  |  |  | 0.86 | 6.8156 | 0.054948 |  | 0.12888
11:33 | 4100 | 6 | 261.4 | 10.4 | 187 | 4.1741 | 0.68902 | 6.2577 |  |  |  |  | 0.87 | 7.229 | 0.070223
11:33 | 4109 | 16 | 261.3 | 10.4 | 188 | 6.8156 | 0.68915 | 6.1814 |  |  |  |  | 0.88 | 7.0253 | 0.071272 |  | 0.14049
11:33 | 4109 | 18 | 261.3 | 10.4 | 189 | 7.229 | 0.68915 | 6.1048 |  |  |  |  | 0.89 | 6.8162 | 0.069208
11:33 | 4111 | 17 | 261.3 | 10.4 | 190 | 7.0253 | 0.68915 | 6.0279 |  |  |  |  | 0.9 | 6.5998 | 0.06708 |  | 0.1312
11:33 | 4111 | 16 | 261.4 | 10.4 | 191 | 6.8162 | 0.68902 | 5.9507 |  |  |  |  | 0.91 | 6.1446 | 0.063722
11:33 | 4106 | 15 | 261.4 | 10.4 | 192 | 6.5998 | 0.68902 | 5.8731 |  |  |  |  | 0.92 | 6.1446 | 0.061446 |  | 0.12289
11:33 | 4105 | 13 | 261.5 | 10.4 | 193 | 6.1446 | 0.68889 | 5.7953 |  |  |  |  | 0.93 | 6.144 | 0.061443
11:33 | 4094 | 13 | 261.5 | 10.4 | 194 | 6.1446 | 0.68889 | 5.7171 |  |  |  |  | 0.94 | 6.1435 | 0.061437 |  | 0.12287
11:33 | 4084 | 13 | 261.4 | 10.4 | 195 | 6.144 | 0.68902 | 5.6387 |  |  |  |  | 0.95 | 6.1435 | 0.061435
11:33 | 4078 | 13 | 261.3 | 10.4 | 196 | 6.1435 | 0.68915 | 5.5599 |  |  |  |  | 0.96 | 6.144 | 0.061437 |  | 0.12208
11:33 | 4069 | 13 | 261.3 | 10.4 | 197 | 6.1435 | 0.68915 | 5.4809 |  |  |  |  | 0.97 | 5.903 | 0.060235
11:33 | 4069 | 13 | 261.4 | 10.4 | 198 | 6.144 | 0.68902 | 5.4016 |  |  |  |  | 0.98 | 5.6512 | 0.057771 |  | 0.11299
11:33 | 4073 | 12 | 261.4 | 10.4 | 199 | 5.903 | 0.68902 | 5.3219 |  |  |  |  | 0.99 | 5.3882 | 0.055197
11:33 | 4073 | 11 | 261.3 | 10.4 | 200 | 5.6512 | 0.68915 | 5.242 |  |  |  |  | 1 | 5.1112 | 0.052497
11:33 | 4075 | 10 | 261.3 | 10.4 | 201 | 5.3882 | 0.68915 | 5.1618
11:33 | 4076 | 9 | 261.2 | 10.4 | 202 | 5.1112 | 0.68928 | 5.0813
11:33 | 4079 | 9 | 261.2 | 10.4 | 203 | 5.1112 | 0.68928 | 5.0005
11:33 | 4082 | 7 | 261.3 | 10.4 | 204 | 4.5081 | 0.68915 | 4.9195
11:33 | 4080 | 7 | 261.3 | 10.4 | 205 | 4.5081 | 0.68915 | 4.8382
11:33 | 4075 | 8 | 261.4 | 10.4 | 206 | 4.8198 | 0.68902 | 4.7566
11:33 | 4074 | 9 | 261.4 | 10.4 | 207 | 5.1121 | 0.68902 | 4.6747
11:33 | 4064 | 9 | 261.4 | 10.4 | 208 | 5.1121 | 0.68902 | 4.5925
11:33 | 4064 | 8 | 261.3 | 10.4 | 209 | 4.8193 | 0.68915 | 4.5101
11:33 | 4057 | 7 | 261.3 | 10.4 | 210 | 4.5081 | 0.68915 | 4.4275
11:33 | 4055 | 4 | 261.3 | 10.4 |  |  | 0.68915
11:33 | 4050 | 4 | 261.3 | 10.4 |  |  | 0.68915
11:33 | 4045 | 6 | 261.4 | 10.4 |  |  | 0.68902
11:33 | 4041 | 6 | 261.4 | 10.4 |  |  | 0.68902
11:33 | 4032 | 6 | 261.4 | 10.4 |  |  | 0.68902
11:33 | 4032 | 6 | 261.2 | 10.4 |  |  | 0.68928
11:33 | 4029 | 4 | 261.2 | 10.4 |  |  | 0.68928
11:33 | 4029 | 2 | 261.2 | 10.4 |  |  | 0.68928
11:33 | 4024 | 2 | 261.2 | 10.4 |  |  | 0.68928
11:33 | 4023 | 1 | 261.1 | 10.4 |  |  | 0.68941
11:33 | 4026 | 1 | 261 | 10.3 |  |  | 0.68954
11:33 | 4029 | -2 | 261 | 10.3 |  |  | 0.68954
11:33 | 4036 | -2 | 261 | 10.3 |  |  | 0.68954
11:33 | 4050 | 0 | 261 | 10.3 |  |  | 0.68954
11:33 | 4050 | 1 | 261 | 10.3 |  |  | 0.68954
11:33 | 4050 | 1 | 260.9 | 10.3 |  |  | 0.68967
11:33 | 4050 | 2 | 260.9 | 10.3 |  |  | 0.68967
11:33 | 4053 | 1 | 260.9 | 10.3 |  |  | 0.68967
11:33 | 4054 | 0 | 260.8 | 10.3 |  |  | 0.6898
11:33 | 4062 | 0 | 260.7 | 10.3 |  |  | 0.68993
11:33 | 4069 | -2 | 260.7 | 10.3 |  |  | 0.68993
11:33 | 4070 | -2 | 260.6 | 10.3 |  |  | 0.69006
11:33 | 4074 | -1 | 260.6 | 10.3 |  |  | 0.69006
11:33 | 4074 | -1 | 260.7 | 10.3 |  |  | 0.68993
11:33 | 4077 | -2 | 260.7 | 10.3 |  |  | 0.68993
11:33 | 4077 | -2 | 260.8 | 10.3 |  |  | 0.6898
11:33 | 4078 | -2 | 260.8 | 10.3 |  |  | 0.6898
11:33 | 4079 | 0 | 260.7 | 10.3 |  |  | 0.68993
11:33 | 4081 | 0 | 260.7 | 10.3 |  |  | 0.68993
11:33 | 4082 | 1 | 260.7 | 10.3 |  |  | 0.68993
11:33 | 4083 | 1 | 260.7 | 10.3 |  |  | 0.68993
11:33 | 4085 | 0 | 260.7 | 10.3 |  |  | 0.68993
11:33 | 4085 | -1 | 260.8 | 10.3 |  |  | 0.6898
11:33 | 4086 | 0 | 260.8 | 10.3 |  |  | 0.6898
11:33 | 4086 | 0 | 260.8 | 10.3 |  |  | 0.6898
11:33 | 4081 | 0 | 260.8 | 10.3 |  |  | 0.6898
11:33 | 4079 | 1 | 260.9 | 10.3 |  |  | 0.68967
11:33 | 4085 | 1 | 261 | 10.3 |  |  | 0.68954
11:33 | 4090 | 4 | 260.9 | 10.3 |  |  | 0.68967
11:33 | 4087 | 4 | 260.9 | 10.3 |  |  | 0.68967
11:33 | 4078 | 6 | 260.9 | 10.3 |  |  | 0.68967
11:33 | 4077 | 8 | 261 | 10.3 |  |  | 0.68954
11:33 | 4062 | 6 | 261 | 10.3 |  |  | 0.68954
11:33 | 4062 | 4 | 261 | 10.3 |  |  | 0.68954
11:33 | 4060 | 4 | 261 | 10.3 |  |  | 0.68954
11:33 | 4059 | 4 | 261 | 10.3 |  |  | 0.68954
11:33 | 4058 | 4 | 261 | 10.3 |  |  | 0.68954
11:33 | 4057 | 2 | 261 | 10.3 |  |  | 0.68954
11:33 | 4059 | 2 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4071 | 3 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4071 | 3 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4072 | 4 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4072 | 4 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4075 | 4 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4077 | 1 | 261.3 | 10.3 |  |  | 0.68915
11:33 | 4080 | 1 | 261.3 | 10.3 |  |  | 0.68915
11:33 | 4083 | 4 | 261.5 | 10.3 |  |  | 0.68889
11:33 | 4080 | 4 | 261.6 | 10.3 |  |  | 0.68877
11:33 | 4068 | 7 | 261.6 | 10.3 |  |  | 0.68877
11:33 | 4068 | 9 | 261.6 | 10.3 |  |  | 0.68877
11:33 | 4064 | 11 | 261.6 | 10.3 |  |  | 0.68877
11:33 | 4064 | 13 | 261.5 | 10.3 |  |  | 0.68889
11:33 | 4074 | 14 | 261.5 | 10.3 |  |  | 0.68889
11:33 | 4081 | 20 | 261.4 | 10.3 |  |  | 0.68902
11:33 | 4078 | 19 | 261.3 | 10.3 |  |  | 0.68915
11:33 | 4075 | 16 | 261.3 | 10.3 |  |  | 0.68915
11:33 | 4075 | 16 | 261.4 | 10.3 |  |  | 0.68902
11:33 | 4075 | 13 | 261.4 | 10.3 |  |  | 0.68902
11:33 | 4075 | 11 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4071 | 15 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4071 | 18 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4064 | 18 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4059 | 18 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4059 | 18 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4060 | 17 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4059 | 17 | 261 | 10.3 |  |  | 0.68954
11:33 | 4043 | 14 | 261 | 10.3 |  |  | 0.68954
11:33 | 4043 | 12 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4032 | 14 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4032 | 16 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4031 | 16 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4030 | 17 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4023 | 17 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4017 | 19 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4016 | 19 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4013 | 19 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4013 | 19 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4032 | 19 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4032 | 19 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4032 | 19 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4031 | 19 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4032 | 19 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4033 | 19 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4032 | 19 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4026 | 20 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4026 | 21 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4023 | 23 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4023 | 26 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4035 | 26 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4045 | 28 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4045 | 28 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4044 | 27 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4044 | 27 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4045 | 27 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4045 | 26 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4055 | 26 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4055 | 27 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4054 | 27 | 261.1 | 10.3 |  |  | 0.68941
11:33 | 4052 | 27 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4055 | 27 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4059 | 29 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4060 | 29 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4068 | 24 | 261.2 | 10.3 |  |  | 0.68928
11:33 | 4068 | 19 | 261.4 | 10.4 |  |  | 0.68902
11:33 | 4073 | 21 | 261.4 | 10.4 |  |  | 0.68902
11:33 | 4073 | 22 | 261.4 | 10.4 |  |  | 0.68902
11:33 | 4069 | 22 | 261.4 | 10.4 |  |  | 0.68902
11:33 | 4066 | 20 | 261.5 | 10.4 |  |  | 0.68889
11:33 | 4064 | 20 | 261.6 | 10.4 |  |  | 0.68877
11:33 | 4062 | 26 | 261.6 | 10.4 |  |  | 0.68877
11:33 | 4062 | 26 | 261.5 | 10.4 |  |  | 0.68889
11:33 | 4058 | 29 | 261.6 | 10.4 |  |  | 0.68877
11:33 | 4058 | 32 | 261.6 | 10.4 |  |  | 0.68877
11:33 | 4066 | 32 | 261.6 | 10.4 |  |  | 0.68877
11:33 | 4067 | 31 | 261.7 | 10.4 |  |  | 0.68864
11:33 | 4068 | 31 | 261.7 | 10.4 |  |  | 0.68864
11:33 | 4070 | 36 | 261.7 | 10.4 |  |  | 0.68864
11:33 | 4073 | 36 | 261.6 | 10.4 |  |  | 0.68877
11:33 | 4077 | 36 | 261.7 | 10.4 |  |  | 0.68864
11:33 | 4077 | 36 | 261.8 | 10.3 |  |  | 0.68851
11:33 | 4076 | 35 | 261.7 | 10.3 |  |  | 0.68864
11:33 | 4076 | 34 | 261.7 | 10.3 |  |  | 0.68864
11:33 | 4068 | 38 | 261.7 | 10.3 |  |  | 0.68864
11:33 | 4067 | 45 | 261.9 | 10.3 |  |  | 0.68838
11:33 | 4065 | 45 | 261.9 | 10.3 |  |  | 0.68838
11:33 | 4062 | 39 | 261.9 | 10.3 |  |  | 0.68838
11:33 | 4062 | 39 | 261.9 | 10.4 |  |  | 0.68838
11:33 | 4061 | 43 | 262 | 10.4 |  |  | 0.68825
11:33 | 4062 | 43 | 262.1 | 10.4 |  |  | 0.68812
11:33 | 4072 | 44 | 262.1 | 10.4 |  |  | 0.68812
11:33 | 4072 | 44 | 261.9 | 10.4 |  |  | 0.68838
11:33 | 4075 | 49 | 261.9 | 10.4 |  |  | 0.68838
11:33 | 4075 | 58 | 262 | 10.4 |  |  | 0.68825
11:33 | 4070 | 57 | 262 | 10.4 |  |  | 0.68825
11:33 | 4065 | 51 | 262 | 10.4 |  |  | 0.68825
11:33 | 4063 | 51 | 262 | 10.4 |  |  | 0.68825
11:33 | 4060 | 54 | 262 | 10.4 |  |  | 0.68825
11:33 | 4060 | 54 | 261.9 | 10.4 |  |  | 0.68838
11:33 | 4060 | 54 | 261.9 | 10.4 |  |  | 0.68838
11:33 | 4060 | 53 | 261.9 | 10.4 |  |  | 0.68838
11:33 | 4063 | 52 | 261.9 | 10.4 |  |  | 0.68838
11:33 | 4063 | 51 | 261.9 | 10.4 |  |  | 0.68838
11:33 | 4064 | 51 | 261.9 | 10.4 |  |  | 0.68838
11:33 | 4064 | 60 | 261.8 | 10.4 |  |  | 0.68851
11:33 | 4061 | 60 | 261.8 | 10.4 |  |  | 0.68851
11:33 | 4056 | 57 | 261.9 | 10.4 |  |  | 0.68838
11:33 | 4056 | 56 | 261.9 | 10.4 |  |  | 0.68838
11:33 | 4053 | 53 | 261.9 | 10.4 |  |  | 0.68838
11:33 | 4053 | 51 | 261.8 | 10.4 |  |  | 0.68851
11:33 | 4052 | 50 | 261.8 | 10.4 |  |  | 0.68851
11:33 | 4052 | 49 | 261.8 | 10.4 |  |  | 0.68851
11:33 | 4045 | 49 | 261.8 | 10.4 |  |  | 0.68851
11:33 | 4038 | 46 | 261.8 | 10.4 |  |  | 0.68851
11:33 | 4035 | 46 | 261.9 | 10.4 |  |  | 0.68838
11:33 | 4031 | 45 | 261.9 | 10.4 |  |  | 0.68838
11:33 | 4030 | 44 | 262 | 10.4 |  |  | 0.68825
11:33 | 4021 | 42 | 262 | 10.4 |  |  | 0.68825
11:33 | 4021 | 40 | 262 | 10.4 |  |  | 0.68825
11:33 | 4012 | 40 | 262 | 10.4 |  |  | 0.68825
11:33 | 4009 | 41 | 261.8 | 10.4 |  |  | 0.68851
11:33 | 4009 | 41 | 261.7 | 10.3 |  |  | 0.68864
11:33 | 4009 | 35 | 261.7 | 10.3 |  |  | 0.68864
11:33 | 4010 | 35 | 261.7 | 10.4 |  |  | 0.68864
11:33 | 4010 | 37 | 261.7 | 10.4 |  |  | 0.68864
11:33 | 4010 | 37 | 261.7 | 10.4 |  |  | 0.68864
11:33 | 4013 | 38 | 261.7 | 10.4 |  |  | 0.68864
11:33 | 4013 | 38 | 261.7 | 10.4 |  |  | 0.68864
11:33 | 4022 | 38 | 261.7 | 10.4 |  |  | 0.68864
11:33 | 4024 | 39 | 261.7 | 10.4 |  |  | 0.68864
11:33 | 4026 | 40 | 261.7 | 10.3 |  |  | 0.68864
11:33 | 4027 | 51 | 261.7 | 10.3 |  |  | 0.68864
11:33 | 4028 | 51 | 261.7 | 10.3 |  |  | 0.68864
11:33 | 4029 | 53 | 261.7 | 10.3 |  |  | 0.68864
11:33 | 4029 | 54 | 261.7 | 10.3 |  |  | 0.68864
11:33 | 4032 | 56 | 261.7 | 10.3 |  |  | 0.68864
11:33 | 4032 | 57 | 261.7 | 10.3 |  |  | 0.68864
11:33 | 4034 | 58 | 261.7 | 10.3 |  |  | 0.68864
11:33 | 4034 | 59 | 261.7 | 10.3 |  |  | 0.68864
11:33 | 4035 | 59 | 261.6 | 10.3 |  |  | 0.68877
11:33 | 4036 | 52 | 261.6 | 10.3 |  |  | 0.68877
11:34 | 4037 | 52 | 261.5 | 10.3 |  |  | 0.68889
11:34 | 4039 | 55 | 261.5 | 10.3 |  |  | 0.68889
11:34 | 4039 | 57 | 261.3 | 10.3 |  |  | 0.68915
11:34 | 4045 | 59 | 261.3 | 10.3 |  |  | 0.68915
11:34 | 4045 | 60 | 261.2 | 10.3 |  |  | 0.68928
11:34 | 4058 | 62 | 261.2 | 10.3 |  |  | 0.68928
11:34 | 4063 | 67 | 261.1 | 10.3 |  |  | 0.68941
11:34 | 4058 | 67 | 261.1 | 10.3 |  |  | 0.68941
11:34 | 4052 | 58 | 261 | 10.3 |  |  | 0.68954
11:34 | 4050 | 58 | 261 | 10.3 |  |  | 0.68954
11:34 | 4043 | 58 | 261 | 10.3 |  |  | 0.68954
11:34 | 4044 | 58 | 261 | 10.3 |  |  | 0.68954
11:34 | 4055 | 60 | 261 | 10.3 |  |  | 0.68954
11:34 | 4055 | 62 | 261.2 | 10.3 |  |  | 0.68928
11:34 | 4053 | 62 | 261.2 | 10.3 |  |  | 0.68928
11:34 | 4053 | 62 | 261.1 | 10.3 |  |  | 0.68941
11:34 | 4057 | 62 | 261 | 10.3 |  |  | 0.68954
11:34 | 4061 | 65 | 261 | 10.3 |  |  | 0.68954
11:34 | 4069 | 65 | 261 | 10.3 |  |  | 0.68954
11:34 | 4091 | 69 | 261 | 10.3 |  |  | 0.68954
11:34 | 4091 | 70 | 260.8 | 10.3 |  |  | 0.6898
11:34 | 4086 | 72 | 260.8 | 10.3 |  |  | 0.6898
11:34 | 4086 | 73 | 260.9 | 10.3 |  |  | 0.68967
11:34 | 4075 | 73 | 260.9 | 10.3 |  |  | 0.68967
11:34 | 4070 | 76 | 261 | 10.3 |  |  | 0.68954
11:34 | 4055 | 76 | 261 | 10.3 |  |  | 0.68954
11:34 | 4042 | 65 | 261 | 10.3 |  |  | 0.68954
11:34 | 4039 | 65 | 261 | 10.3 |  |  | 0.68954
11:34 | 4030 | 62 | 261 | 10.3 |  |  | 0.68954
11:34 | 4031 | 60 | 261.1 | 10.3 |  |  | 0.68941
11:34 | 4043 | 53 | 261.1 | 10.3 |  |  | 0.68941
11:34 | 4043 | 47 | 261.1 | 10.3 |  |  | 0.68941
11:34 | 4042 | 47 | 261.1 | 10.3 |  |  | 0.68941
11:34 | 4042 | 42 | 261.1 | 10.3 |  |  | 0.68941
11:34 | 4040 | 42 | 261.1 | 10.4 |  |  | 0.68941

## P7
| Port | 7
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current
| Pa | Pa | Deg C | mA
Averages | 3975.7898 | 46.3857 | 261.5374 | 10.345 | [11 empty] | 11.849 |  | 11.6802
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current |  |  |  |  | a | b | n | h | xi | f(xi) | Aj
| Pa. | Pa | Deg C | mA |  | 11.5295 |  |  | 0 | 1 | 100 | 0.01 | 0 | 7.4111
[6 empty] | vel | dens | [5 empty] | 0.01 | 7.6036 | 0.075074 |  | 0.15385
11:35 | 3985 | 19 | 259 | 10.3 | 1 | 7.4111 | 0.69213 | 6.3608 |  |  |  |  | 0.02 | 8.3301 | 0.079669
11:35 | 4000 | 20 | 259 | 10.3 | 2 | 7.6036 | 0.69213 | 6.6446 |  |  |  |  | 0.03 | 8.3301 | 0.083301 |  | 0.16602
11:35 | 4009 | 24 | 259.1 | 10.3 | 3 | 8.3301 | 0.692 | 6.9196 |  |  |  |  | 0.04 | 8.1555 | 0.082428
11:35 | 4009 | 24 | 259.1 | 10.3 | 4 | 8.3301 | 0.692 | 7.1858 |  |  |  |  | 0.05 | 7.9762 | 0.080659 |  | 0.1613
11:35 | 4010 | 23 | 259.2 | 10.3 | 5 | 8.1555 | 0.69187 | 7.4435 |  |  |  |  | 0.06 | 8.3309 | 0.081536
11:35 | 4009 | 22 | 259.2 | 10.3 | 6 | 7.9762 | 0.69187 | 7.6927 |  |  |  |  | 0.07 | 8.5011 | 0.08416 |  | 0.16888
11:35 | 3998 | 24 | 259.2 | 10.3 | 7 | 8.3309 | 0.69187 | 7.9337 |  |  |  |  | 0.08 | 8.3293 | 0.084152
11:35 | 3998 | 25 | 259 | 10.3 | 8 | 8.5011 | 0.69213 | 8.1666 |  |  |  |  | 0.09 | 8.3293 | 0.083293 |  | 0.16658
11:35 | 3998 | 24 | 259 | 10.3 | 9 | 8.3293 | 0.69213 | 8.3915 |  |  |  |  | 0.1 | 8.3286 | 0.08329
11:35 | 3998 | 24 | 259 | 10.3 | 10 | 8.3293 | 0.69213 | 8.6086 |  |  |  |  | 0.11 | 8.154 | 0.082413 |  | 0.16366
11:35 | 4001 | 24 | 258.9 | 10.3 | 11 | 8.3286 | 0.69226 | 8.8181 |  |  |  |  | 0.12 | 8.1547 | 0.081544
11:35 | 4004 | 23 | 259 | 10.3 | 12 | 8.154 | 0.69213 | 9.0201 |  |  |  |  | 0.13 | 8.5019 | 0.083283 |  | 0.16944
11:35 | 4012 | 23 | 259.1 | 10.3 | 13 | 8.1547 | 0.692 | 9.2148 |  |  |  |  | 0.14 | 8.6695 | 0.085857
11:35 | 4024 | 25 | 259.1 | 10.3 | 14 | 8.5019 | 0.692 | 9.4023 |  |  |  |  | 0.15 | 8.8346 | 0.08752 |  | 0.17668
11:35 | 4024 | 26 | 259 | 10.3 | 15 | 8.6695 | 0.69213 | 9.5828 |  |  |  |  | 0.16 | 8.9967 | 0.089157
11:35 | 4036 | 27 | 259 | 10.3 | 16 | 8.8346 | 0.69213 | 9.7563 |  |  |  |  | 0.17 | 9.156 | 0.090763 |  | 0.18413
11:35 | 4036 | 28 | 259 | 10.3 | 17 | 8.9967 | 0.69213 | 9.9232 |  |  |  |  | 0.18 | 9.6179 | 0.093869
11:35 | 4051 | 29 | 259 | 10.3 | 18 | 9.156 | 0.69213 | 10.0834 |  |  |  |  | 0.19 | 9.6179 | 0.096179 |  | 0.1943
11:35 | 4054 | 32 | 259 | 10.3 | 19 | 9.6179 | 0.69213 | 10.2371 |  |  |  |  | 0.2 | 10.2013 | 0.099096
11:35 | 4062 | 32 | 259 | 10.3 | 20 | 9.6179 | 0.69213 | 10.3845 |  |  |  |  | 0.21 | 10.2013 | 0.10201 |  | 0.20587
11:35 | 4068 | 36 | 259 | 10.3 | 21 | 10.2013 | 0.69213 | 10.5258 |  |  |  |  | 0.22 | 10.7531 | 0.10477
11:35 | 4071 | 36 | 259 | 10.3 | 22 | 10.2013 | 0.69213 | 10.661 |  |  |  |  | 0.23 | 10.8857 | 0.10819 |  | 0.21771
11:35 | 4077 | 40 | 259 | 10.3 | 23 | 10.7531 | 0.69213 | 10.7903 |  |  |  |  | 0.24 | 11.0177 | 0.10952
11:35 | 4078 | 41 | 258.9 | 10.3 | 24 | 10.8857 | 0.69226 | 10.9138 |  |  |  |  | 0.25 | 11.1522 | 0.11085 |  | 0.2226
11:35 | 4088 | 42 | 258.9 | 10.3 | 25 | 11.0177 | 0.69226 | 11.0317 |  |  |  |  | 0.26 | 11.1522 | 0.11152
11:35 | 4088 | 43 | 259.3 | 10.3 | 26 | 11.1522 | 0.69174 | 11.1441 |  |  |  |  | 0.27 | 11.2833 | 0.11218 |  | 0.22523
11:35 | 4088 | 43 | 259.3 | 10.3 | 27 | 11.1522 | 0.69174 | 11.2511 |  |  |  |  | 0.28 | 11.2833 | 0.11283
11:35 | 4088 | 44 | 259.5 | 10.3 | 28 | 11.2833 | 0.69148 | 11.3529 |  |  |  |  | 0.29 | 11.4129 | 0.11348 |  | 0.22783
11:35 | 4086 | 44 | 259.5 | 10.3 | 29 | 11.2833 | 0.69148 | 11.4495 |  |  |  |  | 0.3 | 11.414 | 0.11413
11:35 | 4084 | 45 | 259.7 | 10.3 | 30 | 11.4129 | 0.69122 | 11.5412 |  |  |  |  | 0.31 | 11.414 | 0.11414 |  | 0.22785
11:35 | 4081 | 45 | 259.8 | 10.3 | 31 | 11.414 | 0.69109 | 11.628 |  |  |  |  | 0.32 | 11.2854 | 0.1135
11:35 | 4076 | 45 | 259.8 | 10.3 | 32 | 11.414 | 0.69109 | 11.7101 |  |  |  |  | 0.33 | 11.414 | 0.1135 |  | 0.22785
11:35 | 4075 | 44 | 259.7 | 10.3 | 33 | 11.2854 | 0.69122 | 11.7875 |  |  |  |  | 0.34 | 11.414 | 0.11414
11:35 | 4059 | 45 | 259.8 | 10.3 | 34 | 11.414 | 0.69109 | 11.8605 |  |  |  |  | 0.35 | 11.5401 | 0.11477 |  | 0.23079
11:35 | 4059 | 45 | 259.8 | 10.3 | 35 | 11.414 | 0.69109 | 11.9291 |  |  |  |  | 0.36 | 11.6638 | 0.11602
11:35 | 4060 | 46 | 259.8 | 10.3 | 36 | 11.5401 | 0.69109 | 11.9935 |  |  |  |  | 0.37 | 11.6627 | 0.11663 |  | 0.23567
11:35 | 4060 | 47 | 259.7 | 10.3 | 37 | 11.6638 | 0.69122 | 12.0537 |  |  |  |  | 0.38 | 12.3859 | 0.12024
11:35 | 4067 | 47 | 259.6 | 10.3 | 38 | 11.6627 | 0.69135 | 12.1099 |  |  |  |  | 0.39 | 12.3859 | 0.12386 |  | 0.24811
11:35 | 4072 | 53 | 259.7 | 10.3 | 39 | 12.3859 | 0.69122 | 12.1622 |  |  |  |  | 0.4 | 12.5022 | 0.12444
11:35 | 4068 | 53 | 259.7 | 10.3 | 40 | 12.3859 | 0.69122 | 12.2107 |  |  |  |  | 0.41 | 12.6175 | 0.1256 |  | 0.2531
11:35 | 4057 | 54 | 259.7 | 10.3 | 41 | 12.5022 | 0.69122 | 12.2556 |  |  |  |  | 0.42 | 12.957 | 0.12787
11:35 | 4057 | 55 | 259.7 | 10.3 | 42 | 12.6175 | 0.69122 | 12.2969 |  |  |  |  | 0.43 | 13.1785 | 0.13068 |  | 0.26283
11:35 | 4044 | 58 | 259.7 | 10.3 | 43 | 12.957 | 0.69122 | 12.3347 |  |  |  |  | 0.44 | 13.1785 | 0.13179
11:35 | 4044 | 60 | 259.7 | 10.3 | 44 | 13.1785 | 0.69122 | 12.3692 |  |  |  |  | 0.45 | 13.3964 | 0.13287 |  | 0.2672
11:35 | 4032 | 60 | 259.7 | 10.4 | 45 | 13.1785 | 0.69122 | 12.4004 |  |  |  |  | 0.46 | 13.3964 | 0.13396
11:35 | 4027 | 62 | 259.7 | 10.4 | 46 | 13.3964 | 0.69122 | 12.4286 |  |  |  |  | 0.47 | 12.957 | 0.13177 |  | 0.2606
11:35 | 4017 | 62 | 259.7 | 10.4 | 47 | 13.3964 | 0.69122 | 12.4537 |  |  |  |  | 0.48 | 12.957 | 0.12957
11:35 | 4007 | 58 | 259.7 | 10.4 | 48 | 12.957 | 0.69122 | 12.4759 |  |  |  |  | 0.49 | 12.5034 | 0.1273 |  | 0.2508
11:35 | 4008 | 58 | 259.7 | 10.4 | 49 | 12.957 | 0.69122 | 12.4952 |  |  |  |  | 0.5 | 12.2708 | 0.12387
11:35 | 4012 | 54 | 259.8 | 10.4 | 50 | 12.5034 | 0.69109 | 12.5119 |  |  |  |  | 0.51 | 12.3883 | 0.1233 |  | 0.24737
11:35 | 4012 | 52 | 259.9 | 10.4 | 51 | 12.2708 | 0.69096 | 12.5259 |  |  |  |  | 0.52 | 12.3883 | 0.12388
11:35 | 4015 | 53 | 259.9 | 10.4 | 52 | 12.3883 | 0.69096 | 12.5374 |  |  |  |  | 0.53 | 12.3883 | 0.12388 |  | 0.24854
11:35 | 4015 | 53 | 259.9 | 10.4 | 53 | 12.3883 | 0.69096 | 12.5465 |  |  |  |  | 0.54 | 12.6198 | 0.12504
11:35 | 4015 | 53 | 259.9 | 10.4 | 54 | 12.3883 | 0.69096 | 12.5532 |  |  |  |  | 0.55 | 12.6186 | 0.12619 |  | 0.25388
11:35 | 4014 | 55 | 259.9 | 10.4 | 55 | 12.6198 | 0.69096 | 12.5577 |  |  |  |  | 0.56 | 13.0707 | 0.12845
11:35 | 4009 | 55 | 259.8 | 10.4 | 56 | 12.6186 | 0.69109 | 12.5601 |  |  |  |  | 0.57 | 13.0707 | 0.13071 |  | 0.25991
11:35 | 4003 | 59 | 259.9 | 10.4 | 57 | 13.0707 | 0.69096 | 12.5604 |  |  |  |  | 0.58 | 12.6198 | 0.12845
11:35 | 4001 | 59 | 259.9 | 10.4 | 58 | 13.0707 | 0.69096 | 12.5588 |  |  |  |  | 0.59 | 12.5046 | 0.12562 |  | 0.2497
11:35 | 3995 | 55 | 259.9 | 10.4 | 59 | 12.6198 | 0.69096 | 12.5553 |  |  |  |  | 0.6 | 12.2708 | 0.12388
11:35 | 3995 | 54 | 259.9 | 10.3 | 60 | 12.5046 | 0.69096 | 12.5499 |  |  |  |  | 0.61 | 12.0314 | 0.12151 |  | 0.24222
11:35 | 3992 | 52 | 259.9 | 10.3 | 61 | 12.2708 | 0.69096 | 12.5429 |  |  |  |  | 0.62 | 12.2697 | 0.12151
11:35 | 3992 | 50 | 259.8 | 10.3 | 62 | 12.0314 | 0.69109 | 12.5343 |  |  |  |  | 0.63 | 13.0707 | 0.1267 |  | 0.25875
11:35 | 3997 | 52 | 259.8 | 10.3 | 63 | 12.2697 | 0.69109 | 12.5241 |  |  |  |  | 0.64 | 13.0719 | 0.13071
11:35 | 4000 | 59 | 259.9 | 10.3 | 64 | 13.0707 | 0.69096 | 12.5125 |  |  |  |  | 0.65 | 12.3894 | 0.12731 |  | 0.25006
11:35 | 3998 | 59 | 260 | 10.3 | 65 | 13.0719 | 0.69083 | 12.4996 |  |  |  |  | 0.66 | 12.3894 | 0.12389
11:35 | 3997 | 53 | 260 | 10.3 | 66 | 12.3894 | 0.69083 | 12.4853 |  |  |  |  | 0.67 | 12.621 | 0.12505 |  | 0.25204
11:35 | 3989 | 53 | 260 | 10.4 | 67 | 12.3894 | 0.69083 | 12.4698 |  |  |  |  | 0.68 | 12.7376 | 0.12679
11:35 | 3966 | 55 | 260 | 10.4 | 68 | 12.621 | 0.69083 | 12.4532 |  |  |  |  | 0.69 | 13.2941 | 0.13016 |  | 0.2651
11:35 | 3964 | 56 | 260.2 | 10.4 | 69 | 12.7376 | 0.69057 | 12.4355 |  |  |  |  | 0.7 | 13.6171 | 0.13456
11:35 | 3924 | 61 | 260.2 | 10.4 | 70 | 13.2941 | 0.69057 | 12.4168 |  |  |  |  | 0.71 | 13.5103 | 0.13564 |  | 0.26874
11:36 | 3924 | 64 | 260.2 | 10.4 | 71 | 13.6171 | 0.69057 | 12.3972 |  |  |  |  | 0.72 | 12.9643 | 0.13237
11:36 | 3908 | 63 | 260.2 | 10.4 | 72 | 13.5103 | 0.69057 | 12.3767 |  |  |  |  | 0.73 | 12.9643 | 0.12964 |  | 0.2562
11:36 | 3899 | 58 | 260.3 | 10.4 | 73 | 12.9643 | 0.69044 | 12.3555 |  |  |  |  | 0.74 | 12.037 | 0.12501
11:36 | 3903 | 58 | 260.3 | 10.4 | 74 | 12.9643 | 0.69044 | 12.3336 |  |  |  |  | 0.75 | 12.0359 | 0.12036 |  | 0.23991
11:36 | 3908 | 50 | 260.3 | 10.4 | 75 | 12.037 | 0.69044 | 12.311 |  |  |  |  | 0.76 | 11.7927 | 0.11914
11:36 | 3909 | 50 | 260.2 | 10.4 | 76 | 12.0359 | 0.69057 | 12.2879 |  |  |  |  | 0.77 | 11.6682 | 0.1173 |  | 0.235
11:36 | 3916 | 48 | 260.2 | 10.4 | 77 | 11.7927 | 0.69057 | 12.2642 |  |  |  |  | 0.78 | 12.0348 | 0.11851
11:36 | 3917 | 47 | 260.1 | 10.4 | 78 | 11.6682 | 0.6907 | 12.2401 |  |  |  |  | 0.79 | 12.2743 | 0.12155 |  | 0.24469
11:36 | 3928 | 50 | 260.1 | 10.4 | 79 | 12.0348 | 0.6907 | 12.2156 |  |  |  |  | 0.8 | 12.2743 | 0.12274
11:36 | 3928 | 52 | 260.2 | 10.4 | 80 | 12.2743 | 0.69057 | 12.1908 |  |  |  |  | 0.81 | 12.0359 | 0.12155 |  | 0.24151
11:36 | 3931 | 52 | 260.2 | 10.4 | 81 | 12.2743 | 0.69057 | 12.1657 |  |  |  |  | 0.82 | 12.0359 | 0.12036
11:36 | 3932 | 50 | 260.2 | 10.4 | 82 | 12.0359 | 0.69057 | 12.1404 |  |  |  |  | 0.83 | 11.6704 | 0.11853 |  | 0.23463
11:36 | 3933 | 50 | 260.2 | 10.4 | 83 | 12.0359 | 0.69057 | 12.1149 |  |  |  |  | 0.84 | 11.6704 | 0.1167
11:36 | 3934 | 47 | 260.3 | 10.4 | 84 | 11.6704 | 0.69044 | 12.0894 |  |  |  |  | 0.85 | 12.037 | 0.11854 |  | 0.24031
11:36 | 3935 | 47 | 260.3 | 10.4 | 85 | 11.6704 | 0.69044 | 12.0638 |  |  |  |  | 0.86 | 12.2731 | 0.12155
11:36 | 3937 | 50 | 260.3 | 10.4 | 86 | 12.037 | 0.69044 | 12.0382 |  |  |  |  | 0.87 | 12.6234 | 0.12448 |  | 0.25207
11:36 | 3937 | 52 | 260.1 | 10.4 | 87 | 12.2731 | 0.6907 | 12.0127 |  |  |  |  | 0.88 | 12.8557 | 0.1274
11:36 | 3939 | 55 | 260.2 | 10.4 | 88 | 12.6234 | 0.69057 | 11.9873 |  |  |  |  | 0.89 | 12.8557 | 0.12856 |  | 0.25711
11:36 | 3939 | 57 | 260.6 | 10.4 | 89 | 12.8557 | 0.69006 | 11.962 |  |  |  |  | 0.9 | 12.8533 | 0.12854
11:36 | 3941 | 57 | 260.6 | 10.4 | 90 | 12.8557 | 0.69006 | 11.9369 |  |  |  |  | 0.91 | 12.7376 | 0.12795 |  | 0.2528
11:36 | 3942 | 57 | 260.4 | 10.4 | 91 | 12.8533 | 0.69031 | 11.9121 |  |  |  |  | 0.92 | 12.037 | 0.12387
11:36 | 3941 | 56 | 260.2 | 10.4 | 92 | 12.7376 | 0.69057 | 11.8876 |  |  |  |  | 0.93 | 12.0382 | 0.12038 |  | 0.24076
11:36 | 3940 | 50 | 260.3 | 10.4 | 93 | 12.037 | 0.69044 | 11.8634 |  |  |  |  | 0.94 | 12.0382 | 0.12038
11:36 | 3938 | 50 | 260.4 | 10.4 | 94 | 12.0382 | 0.69031 | 11.8396 |  |  |  |  | 0.95 | 12.158 | 0.12098 |  | 0.24155
11:36 | 3926 | 50 | 260.4 | 10.4 | 95 | 12.0382 | 0.69031 | 11.8162 |  |  |  |  | 0.96 | 11.795 | 0.11976
11:36 | 3926 | 51 | 260.4 | 10.4 | 96 | 12.158 | 0.69031 | 11.7932 |  |  |  |  | 0.97 | 11.4236 | 0.11609 |  | 0.22971
11:36 | 3912 | 48 | 260.4 | 10.3 | 97 | 11.795 | 0.69031 | 11.7708 |  |  |  |  | 0.98 | 11.4236 | 0.11424
11:36 | 3912 | 45 | 260.7 | 10.3 | 98 | 11.4236 | 0.68993 | 11.7488 |  |  |  |  | 0.99 | 11.4236 | 0.11424 |  | 0.22848
11:36 | 3914 | 45 | 260.7 | 10.3 | 99 | 11.4236 | 0.68993 | 11.7275 |  |  |  |  | 1 | 11.4247 | 0.11424
11:36 | 3916 | 45 | 260.7 | 10.3 | 100 | 11.4236 | 0.68993 | 11.7067 |  |  |  |  | 0 | 11.552 | -11.4884 |  | -11.4157
11:36 | 3920 | 45 | 260.8 | 10.3 | 101 | 11.4247 | 0.6898 | 11.6866 |  |  |  |  | 0.01 | 11.5531 | 0.11553
11:36 | 3924 | 46 | 260.9 | 10.3 | 102 | 11.552 | 0.68967 | 11.6671 |  |  |  |  | 0.02 | 11.17 | 0.11362 |  | 0.2238
11:36 | 3924 | 46 | 261 | 10.3 | 103 | 11.5531 | 0.68954 | 11.6483 |  |  |  |  | 0.03 | 10.9072 | 0.11039
11:36 | 3927 | 43 | 261 | 10.3 | 104 | 11.17 | 0.68954 | 11.6302 |  |  |  |  | 0.04 | 10.7743 | 0.10841 |  | 0.21593
11:36 | 3927 | 41 | 261 | 10.3 | 105 | 10.9072 | 0.68954 | 11.6129 |  |  |  |  | 0.05 | 10.7753 | 0.10775
11:36 | 3931 | 40 | 261.1 | 10.3 | 106 | 10.7743 | 0.68941 | 11.5964 |  |  |  |  | 0.06 | 10.7753 | 0.10775 |  | 0.21683
11:36 | 3931 | 40 | 261.2 | 10.3 | 107 | 10.7753 | 0.68928 | 11.5806 |  |  |  |  | 0.07 | 11.1721 | 0.10974
11:36 | 3932 | 40 | 261.2 | 10.3 | 108 | 10.7753 | 0.68928 | 11.5656 |  |  |  |  | 0.08 | 11.0425 | 0.11107 |  | 0.22128
11:36 | 3933 | 43 | 261.2 | 10.3 | 109 | 11.1721 | 0.68928 | 11.5515 |  |  |  |  | 0.09 | 11.0414 | 0.11042
11:36 | 3942 | 42 | 261.3 | 10.3 | 110 | 11.0425 | 0.68915 | 11.5383 |  |  |  |  | 0.1 | 11.0414 | 0.11041 |  | 0.22126
11:36 | 3951 | 42 | 261.2 | 10.3 | 111 | 11.0414 | 0.68928 | 11.5259 |  |  |  |  | 0.11 | 11.1721 | 0.11107
11:36 | 3952 | 42 | 261.2 | 10.3 | 112 | 11.0414 | 0.68928 | 11.5144 |  |  |  |  | 0.12 | 11.3044 | 0.11238 |  | 0.22565
11:36 | 3962 | 43 | 261.2 | 10.3 | 113 | 11.1721 | 0.68928 | 11.5038 |  |  |  |  | 0.13 | 11.3044 | 0.11304
11:36 | 3962 | 44 | 261.5 | 10.3 | 114 | 11.3044 | 0.68889 | 11.4942 |  |  |  |  | 0.14 | 11.3055 | 0.11305 |  | 0.22611
11:36 | 3963 | 44 | 261.5 | 10.3 | 115 | 11.3044 | 0.68889 | 11.4854 |  |  |  |  | 0.15 | 11.3055 | 0.11305
11:36 | 3963 | 44 | 261.6 | 10.3 | 116 | 11.3055 | 0.68877 | 11.4777 |  |  |  |  | 0.16 | 11.3066 | 0.11306 |  | 0.22613
11:36 | 3961 | 44 | 261.6 | 10.3 | 117 | 11.3055 | 0.68877 | 11.4708 |  |  |  |  | 0.17 | 11.3066 | 0.11307
11:36 | 3960 | 44 | 261.7 | 10.3 | 118 | 11.3066 | 0.68864 | 11.465 |  |  |  |  | 0.18 | 11.3055 | 0.11306 |  | 0.22611
11:36 | 3959 | 44 | 261.7 | 10.3 | 119 | 11.3066 | 0.68864 | 11.4601 |  |  |  |  | 0.19 | 11.3055 | 0.11305
11:36 | 3958 | 44 | 261.6 | 10.3 | 120 | 11.3055 | 0.68877 | 11.4562 |  |  |  |  | 0.2 | 11.3055 | 0.11305 |  | 0.22611
11:36 | 3958 | 44 | 261.6 | 10.3 | 121 | 11.3055 | 0.68877 | 11.4533 |  |  |  |  | 0.21 | 11.3044 | 0.11305
11:36 | 3961 | 44 | 261.6 | 10.3 | 122 | 11.3055 | 0.68877 | 11.4514 |  |  |  |  | 0.22 | 11.3044 | 0.11304 |  | 0.22565
11:36 | 3961 | 44 | 261.5 | 10.3 | 123 | 11.3044 | 0.68889 | 11.4505 |  |  |  |  | 0.23 | 11.1742 | 0.11239
11:36 | 3982 | 44 | 261.5 | 10.3 | 124 | 11.3044 | 0.68889 | 11.4506 |  |  |  |  | 0.24 | 11.3034 | 0.11239 |  | 0.2269
11:36 | 3982 | 43 | 261.4 | 10.3 | 125 | 11.1742 | 0.68902 | 11.4516 |  |  |  |  | 0.25 | 11.6813 | 0.11492
11:36 | 3986 | 44 | 261.4 | 10.3 | 126 | 11.3034 | 0.68902 | 11.4537 |  |  |  |  | 0.26 | 11.6802 | 0.11681 |  | 0.23147
11:36 | 3990 | 47 | 261.3 | 10.3 | 127 | 11.6813 | 0.68915 | 11.4567 |  |  |  |  | 0.27 | 11.0404 | 0.1136
11:36 | 3983 | 47 | 261.2 | 10.3 | 128 | 11.6802 | 0.68928 | 11.4608 |  |  |  |  | 0.28 | 11.0394 | 0.1104 |  | 0.2199
11:36 | 3975 | 42 | 261.1 | 10.3 | 129 | 11.0404 | 0.68941 | 11.4658 |  |  |  |  | 0.29 | 10.7733 | 0.10906
11:36 | 3974 | 42 | 261 | 10.3 | 130 | 11.0394 | 0.68954 | 11.4718 |  |  |  |  | 0.3 | 10.3605 | 0.10567 |  | 0.20996
11:36 | 3956 | 40 | 261 | 10.3 | 131 | 10.7733 | 0.68954 | 11.4787 |  |  |  |  | 0.31 | 10.7723 | 0.10566
11:36 | 3956 | 37 | 260.9 | 10.3 | 132 | 10.3605 | 0.68967 | 11.4866 |  |  |  |  | 0.32 | 11.1711 | 0.10972 |  | 0.22209
11:36 | 3955 | 40 | 260.9 | 10.3 | 133 | 10.7723 | 0.68967 | 11.4955 |  |  |  |  | 0.33 | 11.1711 | 0.11171
11:36 | 3955 | 43 | 261.1 | 10.3 | 134 | 11.1711 | 0.68941 | 11.5053 |  |  |  |  | 0.34 | 11.3013 | 0.11236 |  | 0.22559
11:36 | 3965 | 43 | 261.1 | 10.3 | 135 | 11.1711 | 0.68941 | 11.516 |  |  |  |  | 0.35 | 11.3023 | 0.11302
11:36 | 3973 | 44 | 261.2 | 10.3 | 136 | 11.3013 | 0.68928 | 11.5276 |  |  |  |  | 0.36 | 12.1682 | 0.11735 |  | 0.24048
11:36 | 3984 | 44 | 261.3 | 10.3 | 137 | 11.3023 | 0.68915 | 11.5401 |  |  |  |  | 0.37 | 12.1682 | 0.12168
11:36 | 3995 | 51 | 261.3 | 10.3 | 138 | 12.1682 | 0.68915 | 11.5535 |  |  |  |  | 0.38 | 12.2869 | 0.12228 |  | 0.24612
11:36 | 3996 | 51 | 261.3 | 10.3 | 139 | 12.1682 | 0.68915 | 11.5677 |  |  |  |  | 0.39 | 12.5198 | 0.12403
11:36 | 4006 | 52 | 261.3 | 10.3 | 140 | 12.2869 | 0.68915 | 11.5827 |  |  |  |  | 0.4 | 12.4033 | 0.12462 |  | 0.24806
11:36 | 4006 | 54 | 261.2 | 10.3 | 141 | 12.5198 | 0.68928 | 11.5986 |  |  |  |  | 0.41 | 12.2858 | 0.12345
11:36 | 4007 | 53 | 261.2 | 10.3 | 142 | 12.4033 | 0.68928 | 11.6152 |  |  |  |  | 0.42 | 12.2858 | 0.12286 |  | 0.24688
11:36 | 4007 | 52 | 261.2 | 10.3 | 143 | 12.2858 | 0.68928 | 11.6326 |  |  |  |  | 0.43 | 12.6364 | 0.12461
11:36 | 4005 | 52 | 261.2 | 10.3 | 144 | 12.2858 | 0.68928 | 11.6507 |  |  |  |  | 0.44 | 12.6364 | 0.12636 |  | 0.25077
11:36 | 4004 | 55 | 261.3 | 10.3 | 145 | 12.6364 | 0.68915 | 11.6696 |  |  |  |  | 0.45 | 12.0494 | 0.12343
11:36 | 4001 | 55 | 261.3 | 10.3 | 146 | 12.6364 | 0.68915 | 11.6891 |  |  |  |  | 0.46 | 11.9283 | 0.11989 |  | 0.23856
11:36 | 3998 | 50 | 261.4 | 10.3 | 147 | 12.0494 | 0.68902 | 11.7093 |  |  |  |  | 0.47 | 11.806 | 0.11867
11:36 | 3997 | 49 | 261.4 | 10.3 | 148 | 11.9283 | 0.68902 | 11.7301 |  |  |  |  | 0.48 | 11.6835 | 0.11745 |  | 0.23408
11:36 | 3990 | 48 | 261.4 | 10.3 | 149 | 11.806 | 0.68902 | 11.7514 |  |  |  |  | 0.49 | 11.6835 | 0.11683
11:36 | 3990 | 47 | 261.5 | 10.3 | 150 | 11.6835 | 0.68889 | 11.7734 |  |  |  |  | 0.5 | 11.6846 | 0.11684 |  | 0.23369
11:36 | 3966 | 47 | 261.5 | 10.3 | 151 | 11.6835 | 0.68889 | 11.7958 |  |  |  |  | 0.51 | 11.6846 | 0.11685
11:36 | 3965 | 47 | 261.6 | 10.3 | 152 | 11.6846 | 0.68877 | 11.8187 |  |  |  |  | 0.52 | 11.8082 | 0.11746 |  | 0.23575
11:36 | 3960 | 47 | 261.6 | 10.3 | 153 | 11.6846 | 0.68877 | 11.8421 |  |  |  |  | 0.53 | 11.8082 | 0.11808
11:36 | 3955 | 48 | 261.6 | 10.3 | 154 | 11.8082 | 0.68877 | 11.8659 |  |  |  |  | 0.54 | 11.8071 | 0.11808 |  | 0.23614
11:36 | 3954 | 48 | 261.6 | 10.3 | 155 | 11.8082 | 0.68877 | 11.89 |  |  |  |  | 0.55 | 11.806 | 0.11807
11:36 | 3953 | 48 | 261.5 | 10.3 | 156 | 11.8071 | 0.68889 | 11.9144 |  |  |  |  | 0.56 | 11.9283 | 0.11867 |  | 0.23857
11:36 | 3954 | 48 | 261.4 | 10.3 | 157 | 11.806 | 0.68902 | 11.9392 |  |  |  |  | 0.57 | 12.0517 | 0.1199
11:36 | 3970 | 49 | 261.4 | 10.3 | 158 | 11.9283 | 0.68902 | 11.9641 |  |  |  |  | 0.58 | 11.9306 | 0.11991 |  | 0.23861
11:36 | 3970 | 50 | 261.6 | 10.3 | 159 | 12.0517 | 0.68877 | 11.9893 |  |  |  |  | 0.59 | 11.8082 | 0.11869
11:36 | 3994 | 49 | 261.6 | 10.3 | 160 | 11.9306 | 0.68877 | 12.0146 |  |  |  |  | 0.6 | 11.8082 | 0.11808 |  | 0.23576
11:36 | 3996 | 48 | 261.6 | 10.3 | 161 | 11.8082 | 0.68877 | 12.04 |  |  |  |  | 0.61 | 11.6867 | 0.11747
11:36 | 3998 | 48 | 261.6 | 10.3 | 162 | 11.8082 | 0.68877 | 12.0654 |  |  |  |  | 0.62 | 11.6878 | 0.11687 |  | 0.23334
11:36 | 4000 | 47 | 261.8 | 10.3 | 163 | 11.6867 | 0.68851 | 12.0908 |  |  |  |  | 0.63 | 11.5639 | 0.11626
11:36 | 4001 | 47 | 261.9 | 10.3 | 164 | 11.6878 | 0.68838 | 12.1162 |  |  |  |  | 0.64 | 11.565 | 0.11564 |  | 0.23253
11:36 | 4001 | 46 | 262 | 10.3 | 165 | 11.5639 | 0.68825 | 12.1414 |  |  |  |  | 0.65 | 11.9362 | 0.11751
11:36 | 4001 | 46 | 262.1 | 10.3 | 166 | 11.565 | 0.68812 | 12.1665 |  |  |  |  | 0.66 | 12.2961 | 0.12116 |  | 0.24433
11:36 | 3992 | 49 | 262.1 | 10.3 | 167 | 11.9362 | 0.68812 | 12.1913 |  |  |  |  | 0.67 | 12.1773 | 0.12237
11:36 | 3992 | 52 | 262.1 | 10.3 | 168 | 12.2961 | 0.68812 | 12.2159 |  |  |  |  | 0.68 | 11.935 | 0.12056 |  | 0.23951
11:36 | 3981 | 51 | 262.1 | 10.3 | 169 | 12.1773 | 0.68812 | 12.2401 |  |  |  |  | 0.69 | 11.935 | 0.11935
11:36 | 3980 | 49 | 262 | 10.3 | 170 | 11.935 | 0.68825 | 12.2639 |  |  |  |  | 0.7 | 12.1762 | 0.12056 |  | 0.24272
11:36 | 3984 | 49 | 262 | 10.3 | 171 | 11.935 | 0.68825 | 12.2872 |  |  |  |  | 0.71 | 12.1762 | 0.12176
11:36 | 3987 | 51 | 262 | 10.3 | 172 | 12.1762 | 0.68825 | 12.31 |  |  |  |  | 0.72 | 12.295 | 0.12236 |  | 0.2455
11:36 | 3990 | 51 | 262 | 10.3 | 173 | 12.1762 | 0.68825 | 12.3322 |  |  |  |  | 0.73 | 12.2938 | 0.12294
11:36 | 3993 | 52 | 262 | 10.3 | 174 | 12.295 | 0.68825 | 12.3537 |  |  |  |  | 0.74 | 12.6435 | 0.12469 |  | 0.25285
11:36 | 3993 | 52 | 261.9 | 10.3 | 175 | 12.2938 | 0.68838 | 12.3745 |  |  |  |  | 0.75 | 12.9861 | 0.12815
11:36 | 3994 | 55 | 261.9 | 10.3 | 176 | 12.6435 | 0.68838 | 12.3945 |  |  |  |  | 0.76 | 12.9861 | 0.12986 |  | 0.26008
11:36 | 3994 | 58 | 262.1 | 10.3 | 177 | 12.9861 | 0.68812 | 12.4137 |  |  |  |  | 0.77 | 13.0927 | 0.13039
11:36 | 3979 | 58 | 262.1 | 10.3 | 178 | 12.9861 | 0.68812 | 12.4319 |  |  |  |  | 0.78 | 13.0927 | 0.13093 |  | 0.26148
11:36 | 3977 | 59 | 261.7 | 10.3 | 179 | 13.0927 | 0.68864 | 12.4491 |  |  |  |  | 0.79 | 12.9801 | 0.13036
11:36 | 3967 | 59 | 261.7 | 10.3 | 180 | 13.0927 | 0.68864 | 12.4652 |  |  |  |  | 0.8 | 12.9801 | 0.1298 |  | 0.25847
11:36 | 3958 | 58 | 261.6 | 10.3 | 181 | 12.9801 | 0.68877 | 12.4801 |  |  |  |  | 0.81 | 12.6411 | 0.12811
11:36 | 3957 | 58 | 261.6 | 10.3 | 182 | 12.9801 | 0.68877 | 12.4938 |  |  |  |  | 0.82 | 12.6423 | 0.12642 |  | 0.2536
11:36 | 3956 | 55 | 261.7 | 10.3 | 183 | 12.6411 | 0.68864 | 12.5062 |  |  |  |  | 0.83 | 12.8701 | 0.12756
11:36 | 3957 | 55 | 261.8 | 10.4 | 184 | 12.6423 | 0.68851 | 12.5172 |  |  |  |  | 0.84 | 12.9825 | 0.12926 |  | 0.25965
11:36 | 3965 | 57 | 261.8 | 10.4 | 185 | 12.8701 | 0.68851 | 12.5267 |  |  |  |  | 0.85 | 13.0939 | 0.13038
11:36 | 3965 | 58 | 261.8 | 10.4 | 186 | 12.9825 | 0.68851 | 12.5346 |  |  |  |  | 0.86 | 13.2032 | 0.13149 |  | 0.2637
11:36 | 3960 | 59 | 261.8 | 10.4 | 187 | 13.0939 | 0.68851 | 12.5409 |  |  |  |  | 0.87 | 13.2032 | 0.13203
11:36 | 3958 | 60 | 261.7 | 10.4 | 188 | 13.2032 | 0.68864 | 12.5455 |  |  |  |  | 0.88 | 12.8677 | 0.13035 |  | 0.25847
11:36 | 3960 | 60 | 261.7 | 10.4 | 189 | 13.2032 | 0.68864 | 12.5483 |  |  |  |  | 0.89 | 12.8665 | 0.12867
11:36 | 3961 | 57 | 261.6 | 10.4 | 190 | 12.8677 | 0.68877 | 12.5491 |  |  |  |  | 0.9 | 12.4068 | 0.12637 |  | 0.24967
11:36 | 3968 | 57 | 261.5 | 10.4 | 191 | 12.8665 | 0.68889 | 12.548 |  |  |  |  | 0.91 | 12.408 | 0.12407
11:36 | 3977 | 53 | 261.5 | 10.4 | 192 | 12.4068 | 0.68889 | 12.5448 |  |  |  |  | 0.92 | 12.0517 | 0.1223 |  | 0.241
11:36 | 3978 | 53 | 261.6 | 10.4 | 193 | 12.408 | 0.68877 | 12.5394 |  |  |  |  | 0.93 | 11.6856 | 0.11869
11:36 | 3986 | 50 | 261.6 | 10.3 | 194 | 12.0517 | 0.68877 | 12.5317 |  |  |  |  | 0.94 | 11.8093 | 0.11747 |  | 0.23699
11:36 | 3986 | 47 | 261.7 | 10.3 | 195 | 11.6856 | 0.68864 | 12.5217 |  |  |  |  | 0.95 | 12.175 | 0.11992
11:36 | 3994 | 48 | 261.7 | 10.3 | 196 | 11.8093 | 0.68864 | 12.5092 |  |  |  |  | 0.96 | 12.1762 | 0.12176 |  | 0.24351
11:36 | 3996 | 51 | 261.9 | 10.3 | 197 | 12.175 | 0.68838 | 12.4942 |  |  |  |  | 0.97 | 12.1739 | 0.12175
11:36 | 3993 | 51 | 262 | 10.3 | 198 | 12.1762 | 0.68825 | 12.4765 |  |  |  |  | 0.98 | 12.1728 | 0.12173 |  | 0.24425
11:36 | 3991 | 51 | 261.8 | 10.4 | 199 | 12.1739 | 0.68851 | 12.4561 |  |  |  |  | 0.99 | 12.4091 | 0.12291
11:36 | 3987 | 51 | 261.7 | 10.4 | 200 | 12.1728 | 0.68864 | 12.4328 |  |  |  |  | 1 | 12.5268 | 0.12468
11:36 | 3980 | 53 | 261.7 | 10.4 | 201 | 12.4091 | 0.68864 | 12.4066
11:36 | 3979 | 54 | 261.8 | 10.4 | 202 | 12.5268 | 0.68851 | 12.3773
11:36 | 3978 | 55 | 261.8 | 10.4 | 203 | 12.6423 | 0.68851 | 12.3448
11:36 | 3978 | 56 | 261.8 | 10.4 | 204 | 12.7567 | 0.68851 | 12.3091
11:36 | 3967 | 55 | 261.8 | 10.4 | 205 | 12.6423 | 0.68851 | 12.27
11:36 | 3964 | 52 | 261.6 | 10.4 | 206 | 12.2904 | 0.68877 | 12.2274
11:36 | 3960 | 52 | 261.6 | 10.4 | 207 | 12.2904 | 0.68877 | 12.1812
11:36 | 3956 | 47 | 261.8 | 10.4 | 208 | 11.6867 | 0.68851 | 12.1313
11:36 | 3956 | 47 | 262 | 10.4 | 209 | 11.6889 | 0.68825 | 12.0776
11:36 | 3955 | 45 | 261.9 | 10.4 | 210 | 11.4365 | 0.68838 | 12.0199
11:36 | 3954 | 45 | 261.8 | 10.4 |  | 11.4354 | 0.68851
11:36 | 3947 | 41 | 261.8 | 10.4 |  | 10.9153 | 0.68851
11:36 | 3947 | 37 | 261.7 | 10.4 |  | 10.3682 | 0.68864
11:36 | 3945 | 38 | 261.7 | 10.4 |  | 10.5074 | 0.68864
11:36 | 3944 | 41 | 261.7 | 10.4 |  | 10.9143 | 0.68864
11:36 | 3943 | 41 | 261.7 | 10.4 |  | 10.9143 | 0.68864
11:36 | 3942 | 43 | 261.8 | 10.4 |  | 11.1784 | 0.68851
11:36 | 3942 | 43 | 261.9 | 10.4 |  | 11.1794 | 0.68838
11:36 | 3942 | 43 | 261.9 | 10.4 |  | 11.1794 | 0.68838
11:36 | 3943 | 43 | 261.8 | 10.4 |  | 11.1784 | 0.68851
11:36 | 3954 | 40 | 261.8 | 10.4 |  | 10.7814 | 0.68851
11:36 | 3954 | 37 | 261.9 | 10.4 |  | 10.3702 | 0.68838
11:36 | 3962 | 37 | 261.9 | 10.4 |  | 10.3702 | 0.68838
11:36 | 3964 | 38 | 262 | 10.4 |  | 10.5104 | 0.68825
11:36 | 3966 | 38 | 262 | 10.4 |  | 10.5104 | 0.68825
11:36 | 3967 | 29 | 261.9 | 10.4 |  | 9.1809 | 0.68838
11:36 | 3967 | 29 | 261.8 | 10.4 |  | 9.18 | 0.68851
11:36 | 3969 | 26 | 261.9 | 10.4 |  | 8.693 | 0.68838
11:36 | 3969 | 25 | 262 | 10.4 |  | 8.525 | 0.68825
11:36 | 3965 | 25 | 262 | 10.4 |  | 8.525 | 0.68825
11:36 | 3965 | 26 | 261.8 | 10.4 |  | 8.6922 | 0.68851
11:36 | 3975 | 26 | 261.8 | 10.3 |  | 8.6922 | 0.68851
11:36 | 3979 | 26 | 261.9 | 10.3 |  | 8.693 | 0.68838
11:36 | 3976 | 26 | 261.9 | 10.4 |  | 8.693 | 0.68838
11:36 | 3974 | 26 | 261.9 | 10.4 |  | 8.693 | 0.68838
11:36 | 3973 | 26 | 261.9 | 10.4 |  | 8.693 | 0.68838
11:36 | 3969 | 30 | 261.9 | 10.4 |  | 9.3378 | 0.68838
11:36 | 3969 | 31 | 261.7 | 10.4 |  | 9.4904 | 0.68864
11:36 | 3965 | 33 | 261.7 | 10.4 |  | 9.7918 | 0.68864
11:36 | 3965 | 34 | 261.6 | 10.3 |  | 9.9381 | 0.68877
11:36 | 3952 | 34 | 261.6 | 10.3 |  | 9.9381 | 0.68877
11:36 | 3947 | 34 | 261.8 | 10.3 |  | 9.9399 | 0.68851
11:36 | 3950 | 34 | 262 | 10.3 |  | 9.9418 | 0.68825
11:36 | 3952 | 34 | 262.1 | 10.3 |  | 9.9427 | 0.68812
11:36 | 3957 | 34 | 262.2 | 10.3 |  | 9.9437 | 0.68799
11:36 | 3974 | 38 | 262.2 | 10.3 |  | 10.5123 | 0.68799
11:36 | 3974 | 41 | 262 | 10.3 |  | 10.9174 | 0.68825
11:36 | 3967 | 39 | 262 | 10.3 |  | 10.6478 | 0.68825
11:36 | 3967 | 39 | 261.9 | 10.3 |  | 10.6468 | 0.68838
11:36 | 3958 | 38 | 261.9 | 10.3 |  | 10.5094 | 0.68838
11:36 | 3954 | 36 | 261.9 | 10.3 |  | 10.2291 | 0.68838
11:36 | 3951 | 36 | 261.9 | 10.3 |  | 10.2291 | 0.68838
11:36 | 3949 | 30 | 261.9 | 10.3 |  | 9.3378 | 0.68838
11:36 | 3948 | 30 | 261.9 | 10.3 |  | 9.3378 | 0.68838
11:36 | 3943 | 33 | 261.9 | 10.3 |  | 9.7936 | 0.68838
11:36 | 3943 | 35 | 262.2 | 10.3 |  | 10.0888 | 0.68799
11:36 | 3949 | 34 | 262.2 | 10.3 |  | 9.9437 | 0.68799
11:36 | 3949 | 32 | 262.1 | 10.3 |  | 9.6459 | 0.68812
11:36 | 3947 | 33 | 262.1 | 10.3 |  | 9.7954 | 0.68812
11:36 | 3946 | 38 | 262.3 | 10.3 |  | 10.5133 | 0.68786
11:36 | 3940 | 38 | 262.4 | 10.3 |  | 10.5143 | 0.68774
11:36 | 3934 | 34 | 262.5 | 10.3 |  | 9.9464 | 0.68761
11:36 | 3934 | 34 | 262.6 | 10.3 |  | 9.9474 | 0.68748
11:36 | 3934 | 37 | 262.6 | 10.3 |  | 10.377 | 0.68748
11:36 | 3934 | 39 | 262.5 | 10.3 |  | 10.6527 | 0.68761
11:36 | 3934 | 43 | 262.5 | 10.3 |  | 11.1857 | 0.68761
11:36 | 3934 | 47 | 262.4 | 10.3 |  | 11.6933 | 0.68774
11:36 | 3935 | 47 | 262.4 | 10.3 |  | 11.6933 | 0.68774
11:36 | 3935 | 46 | 262.5 | 10.3 |  | 11.5693 | 0.68761
11:36 | 3944 | 46 | 262.5 | 10.3 |  | 11.5693 | 0.68761
11:36 | 3951 | 45 | 262.5 | 10.3 |  | 11.4429 | 0.68761
11:36 | 3952 | 45 | 262.5 | 10.3 |  | 11.4429 | 0.68761
11:36 | 3953 | 45 | 262.5 | 10.3 |  | 11.4429 | 0.68761
11:36 | 3954 | 45 | 262.5 | 10.3 |  | 11.4429 | 0.68761
11:36 | 3962 | 45 | 262.5 | 10.2 |  | 11.4429 | 0.68761
11:36 | 3962 | 45 | 262.6 | 10.2 |  | 11.4439 | 0.68748
11:36 | 3971 | 45 | 262.6 | 10.2 |  | 11.4439 | 0.68748
11:36 | 3977 | 45 | 262.5 | 10.2 |  | 11.4429 | 0.68761
11:36 | 3987 | 45 | 262.5 | 10.2 |  | 11.4429 | 0.68761
11:36 | 3996 | 45 | 262.5 | 10.2 |  | 11.4429 | 0.68761
11:36 | 3998 | 45 | 262.4 | 10.3 |  | 11.4418 | 0.68774
11:36 | 4022 | 47 | 262.4 | 10.3 |  | 11.6933 | 0.68774
11:36 | 4022 | 49 | 262.4 | 10.3 |  | 11.9395 | 0.68774
11:36 | 4021 | 54 | 262.4 | 10.3 |  | 12.5339 | 0.68774
11:36 | 4021 | 59 | 262.4 | 10.3 |  | 13.1013 | 0.68774
11:36 | 4014 | 59 | 262.4 | 10.4 |  | 13.1013 | 0.68774
11:36 | 4008 | 52 | 262.4 | 10.4 |  | 12.2996 | 0.68774
11:36 | 4008 | 52 | 262.4 | 10.4 |  | 12.2996 | 0.68774
11:36 | 4007 | 54 | 262.3 | 10.4 |  | 12.5327 | 0.68786
11:36 | 4007 | 54 | 262.3 | 10.4 |  | 12.5327 | 0.68786
11:36 | 3997 | 54 | 262.3 | 10.4 |  | 12.5327 | 0.68786
11:36 | 3997 | 53 | 262.3 | 10.4 |  | 12.4161 | 0.68786
11:36 | 3998 | 53 | 262.3 | 10.4 |  | 12.4161 | 0.68786
11:36 | 3998 | 53 | 262.2 | 10.4 |  | 12.4149 | 0.68799
11:36 | 3996 | 53 | 262.2 | 10.4 |  | 12.4149 | 0.68799
11:36 | 3994 | 55 | 262.3 | 10.4 |  | 12.6482 | 0.68786
11:36 | 3990 | 55 | 262.4 | 10.3 |  | 12.6494 | 0.68774
11:36 | 3985 | 56 | 262.5 | 10.3 |  | 12.765 | 0.68761
11:36 | 3985 | 56 | 262.6 | 10.4 |  | 12.7662 | 0.68748
11:36 | 3976 | 56 | 262.6 | 10.4 |  | 12.7662 | 0.68748
11:36 | 3976 | 56 | 262.7 | 10.4 |  | 12.7674 | 0.68735
11:36 | 3962 | 55 | 262.7 | 10.4 |  | 12.6529 | 0.68735
11:36 | 3962 | 54 | 262.5 | 10.4 |  | 12.535 | 0.68761
11:36 | 3956 | 53 | 262.5 | 10.4 |  | 12.4184 | 0.68761
11:36 | 3951 | 50 | 262.7 | 10.4 |  | 12.0641 | 0.68735
11:36 | 3954 | 50 | 262.8 | 10.4 |  | 12.0652 | 0.68722
11:36 | 3957 | 50 | 262.8 | 10.4 |  | 12.0652 | 0.68722
11:36 | 3957 | 50 | 262.8 | 10.4 |  | 12.0652 | 0.68722
11:36 | 3961 | 48 | 262.8 | 10.4 |  | 11.8214 | 0.68722
11:36 | 3961 | 47 | 262.9 | 10.4 |  | 11.6987 | 0.6871
11:36 | 3966 | 49 | 262.9 | 10.4 |  | 11.9451 | 0.6871
11:36 | 3966 | 52 | 262.6 | 10.4 |  | 12.3019 | 0.68748
11:36 | 3962 | 52 | 262.6 | 10.4 |  | 12.3019 | 0.68748
11:36 | 3959 | 51 | 262.7 | 10.4 |  | 12.1841 | 0.68735
11:36 | 3957 | 51 | 262.7 | 10.4 |  | 12.1841 | 0.68735
11:36 | 3955 | 50 | 262.8 | 10.4 |  | 12.0652 | 0.68722
11:36 | 3956 | 50 | 262.8 | 10.4 |  | 12.0652 | 0.68722
11:36 | 3969 | 48 | 262.8 | 10.4 |  | 11.8214 | 0.68722
11:36 | 3969 | 47 | 262.7 | 10.4 |  | 11.6966 | 0.68735
11:36 | 3987 | 49 | 262.7 | 10.4 |  | 11.9428 | 0.68735
11:36 | 3989 | 53 | 262.6 | 10.4 |  | 12.4196 | 0.68748
11:36 | 3991 | 53 | 262.6 | 10.4 |  | 12.4196 | 0.68748
11:36 | 3993 | 53 | 262.6 | 10.4 |  | 12.4196 | 0.68748
11:36 | 3991 | 53 | 262.6 | 10.3 |  | 12.4196 | 0.68748
11:36 | 3988 | 50 | 262.6 | 10.3 |  | 12.063 | 0.68748
11:36 | 3988 | 50 | 262.5 | 10.3 |  | 12.0618 | 0.68761
11:36 | 3982 | 50 | 262.5 | 10.4 |  | 12.0618 | 0.68761
11:36 | 3982 | 50 | 262.2 | 10.3 |  | 12.0585 | 0.68799
11:36 | 3978 | 49 | 262.2 | 10.3 |  | 11.9373 | 0.68799
11:36 | 3978 | 47 | 262.3 | 10.3 |  | 11.6922 | 0.68786
11:36 | 3977 | 47 | 262.3 | 10.3 |  | 11.6922 | 0.68786
11:36 | 3976 | 51 | 262.4 | 10.3 |  | 12.1807 | 0.68774
11:36 | 3971 | 51 | 262.6 | 10.3 |  | 12.183 | 0.68748
11:36 | 3964 | 53 | 262.7 | 10.3 |  | 12.4207 | 0.68735
11:36 | 3964 | 53 | 262.8 | 10.4 |  | 12.4219 | 0.68722
11:36 | 3961 | 51 | 262.8 | 10.4 |  | 12.1853 | 0.68722
11:36 | 3961 | 50 | 262.8 | 10.4 |  | 12.0652 | 0.68722
11:36 | 3959 | 50 | 262.8 | 10.4 |  | 12.0652 | 0.68722
11:36 | 3959 | 51 | 263 | 10.4 |  | 12.1875 | 0.68697
11:36 | 3961 | 51 | 263 | 10.4 |  | 12.1875 | 0.68697
11:36 | 3963 | 48 | 263 | 10.4 |  | 11.8237 | 0.68697
11:36 | 3969 | 48 | 263 | 10.3 |  | 11.8237 | 0.68697
11:36 | 3976 | 48 | 263.1 | 10.3 |  | 11.8248 | 0.68684
11:36 | 3976 | 49 | 263.2 | 10.3 |  | 11.9484 | 0.68671
11:36 | 3977 | 46 | 263.2 | 10.3 |  | 11.5769 | 0.68671
11:36 | 3977 | 45 | 263 | 10.3 |  | 11.4482 | 0.68697
11:36 | 3975 | 46 | 263 | 10.3 |  | 11.5747 | 0.68697
11:36 | 3975 | 48 | 262.9 | 10.3 |  | 11.8225 | 0.6871
11:36 | 3972 | 47 | 262.9 | 10.3 |  | 11.6987 | 0.6871
11:36 | 3969 | 46 | 262.9 | 10.3 |  | 11.5736 | 0.6871
11:36 | 3969 | 46 | 262.9 | 10.4 |  | 11.5736 | 0.6871
11:36 | 3970 | 49 | 262.9 | 10.4 |  | 11.9451 | 0.6871
11:36 | 3970 | 49 | 262.9 | 10.4 |  | 11.9451 | 0.6871
11:36 | 3977 | 48 | 262.9 | 10.4 |  | 11.8225 | 0.6871
11:36 | 3977 | 47 | 262.6 | 10.4 |  | 11.6955 | 0.68748
11:36 | 3977 | 48 | 262.6 | 10.3 |  | 11.8192 | 0.68748
11:36 | 3977 | 50 | 262.5 | 10.4 |  | 12.0618 | 0.68761
11:36 | 3972 | 50 | 262.5 | 10.4 |  | 12.0618 | 0.68761
11:36 | 3967 | 52 | 262.5 | 10.4 |  | 12.3007 | 0.68761
11:36 | 3966 | 52 | 262.5 | 10.4 |  | 12.3007 | 0.68761
11:36 | 3965 | 45 | 262.5 | 10.4 |  | 11.4429 | 0.68761
11:36 | 3965 | 44 | 262.5 | 10.4 |  | 11.315 | 0.68761
11:36 | 3969 | 44 | 262.6 | 10.4 |  | 11.3161 | 0.68748
11:36 | 3969 | 44 | 262.8 | 10.3 |  | 11.3182 | 0.68722
11:36 | 3965 | 45 | 262.8 | 10.3 |  | 11.4461 | 0.68722
11:36 | 3964 | 46 | 262.6 | 10.3 |  | 11.5704 | 0.68748
11:36 | 3975 | 46 | 262.6 | 10.3 |  | 11.5704 | 0.68748
11:36 | 3984 | 47 | 262.7 | 10.3 |  | 11.6966 | 0.68735
11:36 | 3991 | 47 | 262.7 | 10.4 |  | 11.6966 | 0.68735
11:36 | 4001 | 47 | 262.7 | 10.4 |  | 11.6966 | 0.68735
11:36 | 4001 | 47 | 262.8 | 10.4 |  | 11.6977 | 0.68722
11:36 | 4010 | 47 | 262.8 | 10.4 |  | 11.6977 | 0.68722
11:36 | 4010 | 47 | 262.7 | 10.4 |  | 11.6966 | 0.68735
11:36 | 4003 | 47 | 262.7 | 10.3 |  | 11.6966 | 0.68735
11:36 | 4000 | 47 | 262.7 | 10.3 |  | 11.6966 | 0.68735
11:37 | 3990 | 47 | 262.7 | 10.3 |  | 11.6966 | 0.68735
11:37 | 3980 | 50 | 262.8 | 10.3 |  | 12.0652 | 0.68722
11:37 | 3973 | 50 | 262.8 | 10.4 |  | 12.0652 | 0.68722
11:37 | 3961 | 55 | 262.8 | 10.4 |  | 12.6541 | 0.68722
11:37 | 3960 | 57 | 262.7 | 10.4 |  | 12.8809 | 0.68735
11:37 | 3951 | 57 | 262.7 | 10.4 |  | 12.8809 | 0.68735
11:37 | 3951 | 57 | 262.7 | 10.3 |  | 12.8809 | 0.68735
11:37 | 3943 | 55 | 262.7 | 10.3 |  | 12.6529 | 0.68735
11:37 | 3940 | 48 | 262.7 | 10.3 |  | 11.8203 | 0.68735
11:37 | 3944 | 48 | 262.7 | 10.3 |  | 11.8203 | 0.68735
11:37 | 3947 | 46 | 262.7 | 10.3 |  | 11.5715 | 0.68735
11:37 | 3945 | 46 | 262.7 | 10.3 |  | 11.5715 | 0.68735
11:37 | 3941 | 49 | 262.7 | 10.3 |  | 11.9428 | 0.68735
11:37 | 3940 | 50 | 262.7 | 10.3 |  | 12.0641 | 0.68735
11:37 | 3923 | 52 | 262.7 | 10.3 |  | 12.303 | 0.68735
11:37 | 3923 | 54 | 262.6 | 10.3 |  | 12.5362 | 0.68748
11:37 | 3925 | 54 | 262.6 | 10.4 |  | 12.5362 | 0.68748
11:37 | 3926 | 53 | 262.5 | 10.4 |  | 12.4184 | 0.68761
11:37 | 3927 | 53 | 262.4 | 10.4 |  | 12.4173 | 0.68774
11:37 | 3929 | 52 | 262.4 | 10.4 |  | 12.2996 | 0.68774
11:37 | 3929 | 52 | 262.5 | 10.4 |  | 12.3007 | 0.68761
11:37 | 3931 | 49 | 262.4 | 10.4 |  | 11.9395 | 0.68774
11:37 | 3931 | 48 | 262.3 | 10.4 |  | 11.8159 | 0.68786
11:37 | 3933 | 45 | 262.3 | 10.4 |  | 11.4407 | 0.68786
11:37 | 3933 | 42 | 262.2 | 10.4 |  | 11.0518 | 0.68799
11:37 | 3935 | 44 | 262.2 | 10.4 |  | 11.3118 | 0.68799
11:37 | 3936 | 49 | 262 | 10.4 |  | 11.935 | 0.68825
11:37 | 3944 | 49 | 261.9 | 10.4 |  | 11.9339 | 0.68838
11:37 | 3952 | 49 | 262 | 10.4 |  | 11.935 | 0.68825
11:37 | 3955 | 49 | 262 | 10.4 |  | 11.935 | 0.68825
11:37 | 3962 | 51 | 262 | 10.4 |  | 12.1762 | 0.68825
11:37 | 3962 | 51 | 262 | 10.4 |  | 12.1762 | 0.68825
11:37 | 3967 | 52 | 262 | 10.4 |  | 12.295 | 0.68825
11:37 | 3967 | 52 | 261.8 | 10.4 |  | 12.2927 | 0.68851
11:37 | 3968 | 52 | 261.8 | 10.4 |  | 12.2927 | 0.68851
11:37 | 3968 | 54 | 261.7 | 10.4 |  | 12.5257 | 0.68864
11:37 | 3966 | 55 | 261.6 | 10.4 |  | 12.6399 | 0.68877
11:37 | 3965 | 58 | 261.5 | 10.4 |  | 12.9789 | 0.68889
11:37 | 3968 | 58 | 261.5 | 10.4 |  | 12.9789 | 0.68889
11:37 | 3978 | 55 | 261.5 | 10.4 |  | 12.6387 | 0.68889
11:37 | 3979 | 54 | 261.7 | 10.4 |  | 12.5257 | 0.68864
11:37 | 3986 | 54 | 261.7 | 10.4 |  | 12.5257 | 0.68864
11:37 | 3986 | 54 | 261.5 | 10.4 |  | 12.5233 | 0.68889
11:37 | 3985 | 53 | 261.5 | 10.4 |  | 12.4068 | 0.68889
11:37 | 3984 | 45 | 261.6 | 10.4 |  | 11.4332 | 0.68877
11:37 | 3993 | 45 | 261.6 | 10.4 |  | 11.4332 | 0.68877
11:37 | 4001 | 42 | 261.5 | 10.4 |  | 11.0445 | 0.68889
11:37 | 4002 | 42 | 261.5 | 10.4 |  | 11.0445 | 0.68889
11:37 | 4006 | 40 | 261.5 | 10.4 |  | 10.7784 | 0.68889
11:37 | 4006 | 39 | 261.7 | 10.4 |  | 10.6448 | 0.68864
11:37 | 4002 | 35 | 261.7 | 10.4 |  | 10.0841 | 0.68864
11:37 | 4002 | 31 | 261.9 | 10.4 |  | 9.4922 | 0.68838
11:37 | 4008 | 31 | 261.9 | 10.4 |  | 9.4922 | 0.68838
11:37 | 4012 | 32 | 261.9 | 10.4 |  | 9.6441 | 0.68838
11:37 | 3999 | 32 | 261.9 | 10.4 |  | 9.6441 | 0.68838
11:37 | 3987 | 30 | 262 | 10.4 |  | 9.3387 | 0.68825
11:37 | 3987 | 30 | 262.1 | 10.4 |  | 9.3396 | 0.68812
11:37 | 3983 | 24 | 262.1 | 10.4 |  | 8.3536 | 0.68812
11:37 | 3983 | 20 | 262 | 10.4 |  | 7.625 | 0.68825
11:37 | 3985 | 21 | 262 | 10.4 |  | 7.8133 | 0.68825

## P8
| Port | 8
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current |  |  |  |  | = 1.111301757081E-11x6 - 6.824575612664E-09x5 + 1.585707016614E-06x4 - 1.688756766696E-04x3 + 7.005244345137E-03x2 + 6.926395307573E-02x + 5.000000000000E+00
| Pa | Pa | Deg C | mA
Averages | 3958.9584 | 55.9654 | 263.3035 | 10.3256 | [12 empty] | 10.3842 |  | 10.68
Time | Static Pressure | Velocity Pressure | Duct Air Temperature | Piccolo Tx Current | [5 empty] | a | b | n | h | xi | f(xi) | Aj
| Pa. | Pa | Deg C | mA |  | 12.5827 |  |  |  | 0 | 1 | 100 | 0.01 | 0 | 6.1435
[6 empty] | vel | dens | [6 empty] | 0.01 | 6.1435 | 0.061435 |  | 0.12511
11:38 | 3994 | 13 | 261.3 | 10.4 | 1 | 6.1435 | 0.68915 | 5.0761 | [5 empty] | 0.02 | 6.8156 | 0.064795
11:38 | 3985 | 13 | 261.3 | 10.4 | 2 | 6.1435 | 0.68915 | 5.1652 | [5 empty] | 0.03 | 6.8156 | 0.068156 |  | 0.13484
11:38 | 3980 | 16 | 261.3 | 10.4 | 3 | 6.8156 | 0.68915 | 5.2664 | [5 empty] | 0.04 | 6.3754 | 0.065955
11:38 | 3977 | 16 | 261.3 | 10.4 | 4 | 6.8156 | 0.68915 | 5.3787 | [5 empty] | 0.05 | 6.3754 | 0.063754 |  | 0.12825
11:38 | 3973 | 14 | 261.3 | 10.4 | 5 | 6.3754 | 0.68915 | 5.5013 | [5 empty] | 0.06 | 6.5991 | 0.064873
11:38 | 3972 | 14 | 261.3 | 10.4 | 6 | 6.3754 | 0.68915 | 5.6333 | [5 empty] | 0.07 | 6.5979 | 0.065985 |  | 0.13196
11:38 | 3963 | 15 | 261.3 | 10.4 | 7 | 6.5991 | 0.68915 | 5.7739 | [5 empty] | 0.08 | 6.5979 | 0.065979
11:38 | 3963 | 15 | 261.1 | 10.4 | 8 | 6.5979 | 0.68941 | 5.9223 | [5 empty] | 0.09 | 6.144 | 0.06371 |  | 0.1244
11:38 | 3952 | 15 | 261.1 | 10.4 | 9 | 6.5979 | 0.68941 | 6.0777 | [5 empty] | 0.1 | 6.1446 | 0.061443
11:38 | 3950 | 13 | 261.4 | 10.4 | 10 | 6.144 | 0.68902 | 6.2395 | [5 empty] | 0.11 | 6.376 | 0.062603 |  | 0.12675
11:38 | 3953 | 13 | 261.5 | 10.4 | 11 | 6.1446 | 0.68889 | 6.4069 | [5 empty] | 0.12 | 6.3754 | 0.063757
11:38 | 3956 | 14 | 261.4 | 10.4 | 12 | 6.376 | 0.68902 | 6.5793 | [5 empty] | 0.13 | 6.5998 | 0.064876 |  | 0.13197
11:38 | 3955 | 14 | 261.3 | 10.4 | 13 | 6.3754 | 0.68915 | 6.7561 | [5 empty] | 0.14 | 6.8175 | 0.067086
11:38 | 3953 | 15 | 261.4 | 10.4 | 14 | 6.5998 | 0.68902 | 6.9367 | [5 empty] | 0.15 | 7.0273 | 0.069224 |  | 0.13985
11:38 | 3952 | 16 | 261.6 | 10.4 | 15 | 6.8175 | 0.68877 | 7.1204 | [5 empty] | 0.16 | 7.0279 | 0.070276
11:38 | 3943 | 17 | 261.6 | 10.4 | 16 | 7.0273 | 0.68877 | 7.3068 | [5 empty] | 0.17 | 7.2317 | 0.071298 |  | 0.14462
11:38 | 3943 | 17 | 261.7 | 10.4 | 17 | 7.0279 | 0.68864 | 7.4953 | [5 empty] | 0.18 | 7.4313 | 0.073315
11:38 | 3937 | 18 | 261.7 | 10.4 | 18 | 7.2317 | 0.68864 | 7.6855 | [5 empty] | 0.19 | 7.4319 | 0.074316 |  | 0.1473
11:38 | 3936 | 19 | 261.9 | 10.4 | 19 | 7.4313 | 0.68838 | 7.8769 | [5 empty] | 0.2 | 7.0306 | 0.072313
11:38 | 3937 | 19 | 262 | 10.4 | 20 | 7.4319 | 0.68825 | 8.069 | [5 empty] | 0.21 | 7.0306 | 0.070306 |  | 0.1426
11:38 | 3937 | 17 | 262.1 | 10.4 | 21 | 7.0306 | 0.68812 | 8.2614 | [5 empty] | 0.22 | 7.6257 | 0.073281
11:38 | 3939 | 17 | 262.1 | 10.4 | 22 | 7.0306 | 0.68812 | 8.4537 | [5 empty] | 0.23 | 7.6257 | 0.076257 |  | 0.15314
11:38 | 3942 | 20 | 262.1 | 10.4 | 23 | 7.6257 | 0.68812 | 8.6456 | [5 empty] | 0.24 | 7.814 | 0.077199
11:38 | 3942 | 20 | 262.1 | 10.4 | 24 | 7.6257 | 0.68812 | 8.8367 | [5 empty] | 0.25 | 7.8148 | 0.078144 |  | 0.15809
11:38 | 3938 | 21 | 262.1 | 10.4 | 25 | 7.814 | 0.68812 | 9.0267 | [5 empty] | 0.26 | 8.3543 | 0.080846
11:38 | 3938 | 21 | 262.2 | 10.4 | 26 | 7.8148 | 0.68799 | 9.2152 | [5 empty] | 0.27 | 9.4948 | 0.089246 |  | 0.1861
11:38 | 3932 | 24 | 262.2 | 10.4 | 27 | 8.3543 | 0.68799 | 9.4021 | [5 empty] | 0.28 | 9.4957 | 0.094953
11:38 | 3931 | 31 | 262.2 | 10.4 | 28 | 9.4948 | 0.68799 | 9.5869 | [5 empty] | 0.29 | 9.9427 | 0.097192 |  | 0.19736
11:38 | 3927 | 31 | 262.3 | 10.4 | 29 | 9.4957 | 0.68786 | 9.7695 | [5 empty] | 0.3 | 9.9418 | 0.099423
11:38 | 3923 | 34 | 262.1 | 10.4 | 30 | 9.9427 | 0.68812 | 9.9497 | [5 empty] | 0.31 | 10.5113 | 0.10227 |  | 0.20879
11:38 | 3923 | 34 | 262 | 10.4 | 31 | 9.9418 | 0.68825 | 10.1272 | [5 empty] | 0.32 | 10.6497 | 0.10581
11:38 | 3923 | 38 | 262.1 | 10.4 | 32 | 10.5113 | 0.68812 | 10.3018 | [5 empty] | 0.33 | 11.1826 | 0.10916 |  | 0.22316
11:38 | 3924 | 39 | 262.2 | 10.4 | 33 | 10.6497 | 0.68799 | 10.4733 | [5 empty] | 0.34 | 11.5682 | 0.11375
11:38 | 3929 | 43 | 262.2 | 10.3 | 34 | 11.1826 | 0.68799 | 10.6417 | [5 empty] | 0.35 | 11.6933 | 0.11631 |  | 0.23468
11:38 | 3929 | 46 | 262.4 | 10.3 | 35 | 11.5682 | 0.68774 | 10.8067 | [5 empty] | 0.36 | 12.0618 | 0.11878
11:38 | 3931 | 47 | 262.4 | 10.3 | 36 | 11.6933 | 0.68774 | 10.9681 | [5 empty] | 0.37 | 12.063 | 0.12062 |  | 0.24205
11:38 | 3932 | 50 | 262.5 | 10.3 | 37 | 12.0618 | 0.68761 | 11.126 | [5 empty] | 0.38 | 12.3019 | 0.12182
11:38 | 3936 | 50 | 262.6 | 10.3 | 38 | 12.063 | 0.68748 | 11.2802 | [5 empty] | 0.39 | 12.303 | 0.12302 |  | 0.24722
11:38 | 3940 | 52 | 262.6 | 10.3 | 39 | 12.3019 | 0.68748 | 11.4305 | [5 empty] | 0.4 | 12.6529 | 0.12478
11:38 | 3942 | 52 | 262.7 | 10.3 | 40 | 12.303 | 0.68735 | 11.577 | [5 empty] | 0.41 | 12.7662 | 0.1271 |  | 0.25607
11:38 | 3947 | 55 | 262.7 | 10.3 | 41 | 12.6529 | 0.68735 | 11.7195 | [5 empty] | 0.42 | 13.1037 | 0.12935
11:38 | 3946 | 56 | 262.6 | 10.3 | 42 | 12.7662 | 0.68748 | 11.858 | [5 empty] | 0.43 | 13.3215 | 0.13213 |  | 0.26534
11:38 | 3940 | 59 | 262.6 | 10.3 | 43 | 13.1037 | 0.68748 | 11.9924 | [5 empty] | 0.44 | 13.2118 | 0.13267
11:38 | 3940 | 61 | 262.4 | 10.3 | 44 | 13.3215 | 0.68774 | 12.1228 | [5 empty] | 0.45 | 13.1013 | 0.13157 |  | 0.26202
11:38 | 3940 | 60 | 262.4 | 10.3 | 45 | 13.2118 | 0.68774 | 12.249 | [5 empty] | 0.46 | 12.9898 | 0.13046
11:38 | 3941 | 59 | 262.4 | 10.3 | 46 | 13.1013 | 0.68774 | 12.3712 | [5 empty] | 0.47 | 12.8773 | 0.12934 |  | 0.25792
11:38 | 3944 | 58 | 262.4 | 10.3 | 47 | 12.9898 | 0.68774 | 12.4892 | [5 empty] | 0.48 | 12.8773 | 0.12877
11:38 | 3947 | 57 | 262.4 | 10.3 | 48 | 12.8773 | 0.68774 | 12.603 | [5 empty] | 0.49 | 12.7639 | 0.12821 |  | 0.25565
11:38 | 3947 | 57 | 262.4 | 10.3 | 49 | 12.8773 | 0.68774 | 12.7128 | [5 empty] | 0.5 | 12.7627 | 0.12763
11:38 | 3947 | 56 | 262.4 | 10.3 | 50 | 12.7639 | 0.68774 | 12.8185 | [5 empty] | 0.51 | 13.1001 | 0.12931 |  | 0.26162
11:38 | 3947 | 56 | 262.3 | 10.3 | 51 | 12.7627 | 0.68786 | 12.9201 | [5 empty] | 0.52 | 13.324 | 0.13212
11:38 | 3943 | 59 | 262.3 | 10.3 | 52 | 13.1001 | 0.68786 | 13.0177 | [5 empty] | 0.53 | 13.4327 | 0.13378 |  | 0.26936
11:38 | 3943 | 61 | 262.6 | 10.3 | 53 | 13.324 | 0.68748 | 13.1113 | [5 empty] | 0.54 | 13.7526 | 0.13593
11:38 | 3935 | 62 | 262.6 | 10.3 | 54 | 13.4327 | 0.68748 | 13.201 | [5 empty] | 0.55 | 13.7526 | 0.13753 |  | 0.27434
11:38 | 3932 | 65 | 262.5 | 10.3 | 55 | 13.7526 | 0.68761 | 13.2868 | [5 empty] | 0.56 | 13.5394 | 0.13646
11:38 | 3933 | 65 | 262.5 | 10.3 | 56 | 13.7526 | 0.68761 | 13.3688 | [5 empty] | 0.57 | 13.5381 | 0.13539 |  | 0.27041
11:38 | 3933 | 63 | 262.5 | 10.3 | 57 | 13.5394 | 0.68761 | 13.4471 | [5 empty] | 0.58 | 13.4302 | 0.13484
11:38 | 3938 | 63 | 262.4 | 10.4 | 58 | 13.5381 | 0.68774 | 13.5216 | [5 empty] | 0.59 | 13.4302 | 0.1343 |  | 0.26896
11:38 | 3949 | 62 | 262.4 | 10.4 | 59 | 13.4302 | 0.68774 | 13.5926 | [5 empty] | 0.6 | 13.5381 | 0.13484
11:38 | 3949 | 62 | 262.4 | 10.3 | 60 | 13.4302 | 0.68774 | 13.66 | [5 empty] | 0.61 | 13.7513 | 0.13645 |  | 0.27432
11:38 | 3957 | 63 | 262.4 | 10.3 | 61 | 13.5381 | 0.68774 | 13.724 | [5 empty] | 0.62 | 13.7513 | 0.13751
11:38 | 3957 | 65 | 262.4 | 10.3 | 62 | 13.7513 | 0.68774 | 13.7847 | [5 empty] | 0.63 | 14.0651 | 0.13908 |  | 0.28026
11:38 | 3962 | 65 | 262.4 | 10.3 | 63 | 13.7513 | 0.68774 | 13.842 | [5 empty] | 0.64 | 14.0651 | 0.14065
11:38 | 3965 | 68 | 262.4 | 10.3 | 64 | 14.0651 | 0.68774 | 13.8962 | [5 empty] | 0.65 | 14.0638 | 0.14064 |  | 0.28128
11:38 | 3960 | 68 | 262.4 | 10.3 | 65 | 14.0651 | 0.68774 | 13.9473 | [5 empty] | 0.66 | 14.0625 | 0.14063
11:38 | 3956 | 68 | 262.3 | 10.3 | 66 | 14.0638 | 0.68786 | 13.9955 | [5 empty] | 0.67 | 14.0638 | 0.14063 |  | 0.28128
11:38 | 3953 | 68 | 262.2 | 10.3 | 67 | 14.0625 | 0.68799 | 14.0407 | [5 empty] | 0.68 | 14.0664 | 0.14065
11:38 | 3941 | 68 | 262.3 | 10.3 | 68 | 14.0638 | 0.68786 | 14.0831 | [5 empty] | 0.69 | 13.4327 | 0.1375 |  | 0.26893
11:38 | 3942 | 68 | 262.5 | 10.4 | 69 | 14.0664 | 0.68761 | 14.1229 | [5 empty] | 0.7 | 12.8821 | 0.13157
11:38 | 3948 | 62 | 262.6 | 10.4 | 70 | 13.4327 | 0.68748 | 14.16 | [5 empty] | 0.71 | 13.1062 | 0.12994 |  | 0.26459
11:38 | 3948 | 57 | 262.8 | 10.4 | 71 | 12.8821 | 0.68722 | 14.1947 | [5 empty] | 0.72 | 14.0703 | 0.13588
11:38 | 3959 | 59 | 262.8 | 10.4 | 72 | 13.1062 | 0.68722 | 14.227 | [5 empty] | 0.73 | 14.0703 | 0.1407 |  | 0.28277
11:38 | 3965 | 68 | 262.8 | 10.4 | 73 | 14.0703 | 0.68722 | 14.2569 | [5 empty] | 0.74 | 14.4783 | 0.14274
11:38 | 3965 | 68 | 262.8 | 10.3 | 74 | 14.0703 | 0.68722 | 14.2847 | [5 empty] | 0.75 | 14.4796 | 0.14479 |  | 0.28925
11:38 | 3964 | 72 | 262.8 | 10.3 | 75 | 14.4783 | 0.68722 | 14.3105 | [5 empty] | 0.76 | 14.3787 | 0.14429
11:38 | 3967 | 72 | 262.9 | 10.3 | 76 | 14.4796 | 0.6871 | 14.3342 | [5 empty] | 0.77 | 14.376 | 0.14377 |  | 0.28719
11:38 | 3975 | 71 | 262.9 | 10.3 | 77 | 14.3787 | 0.6871 | 14.3561 | [5 empty] | 0.78 | 14.2744 | 0.14325
11:38 | 3975 | 71 | 262.7 | 10.3 | 78 | 14.376 | 0.68735 | 14.3761 | [5 empty] | 0.79 | 14.1708 | 0.14223 |  | 0.28376
11:38 | 3970 | 70 | 262.7 | 10.3 | 79 | 14.2744 | 0.68735 | 14.3945 | [5 empty] | 0.8 | 14.1708 | 0.14171
11:38 | 3970 | 69 | 262.6 | 10.3 | 80 | 14.1708 | 0.68748 | 14.4113 | [5 empty] | 0.81 | 13.9639 | 0.14067 |  | 0.27997
11:38 | 3972 | 69 | 262.6 | 10.3 | 81 | 14.1708 | 0.68748 | 14.4266 | [5 empty] | 0.82 | 13.9652 | 0.13965
11:38 | 3974 | 67 | 262.6 | 10.3 | 82 | 13.9639 | 0.68748 | 14.4405 | [5 empty] | 0.83 | 13.858 | 0.13912 |  | 0.27751
11:38 | 3977 | 67 | 262.7 | 10.3 | 83 | 13.9652 | 0.68735 | 14.4531 | [5 empty] | 0.84 | 13.8567 | 0.13857
11:38 | 3981 | 66 | 262.5 | 10.3 | 84 | 13.858 | 0.68761 | 14.4645 | [5 empty] | 0.85 | 14.0651 | 0.13961 |  | 0.28062
11:38 | 3981 | 66 | 262.4 | 10.3 | 85 | 13.8567 | 0.68774 | 14.4747 | [5 empty] | 0.86 | 14.069 | 0.14067
11:38 | 3980 | 68 | 262.4 | 10.3 | 86 | 14.0651 | 0.68774 | 14.4839 | [5 empty] | 0.87 | 13.9652 | 0.14017 |  | 0.27965
11:38 | 3980 | 68 | 262.7 | 10.3 | 87 | 14.069 | 0.68735 | 14.4921 | [5 empty] | 0.88 | 13.9639 | 0.13965
11:38 | 3979 | 67 | 262.7 | 10.3 | 88 | 13.9652 | 0.68735 | 14.4994 | [5 empty] | 0.89 | 13.9639 | 0.13964 |  | 0.27962
11:38 | 3979 | 67 | 262.6 | 10.3 | 89 | 13.9639 | 0.68748 | 14.5059 | [5 empty] | 0.9 | 14.0664 | 0.14015
11:38 | 3975 | 67 | 262.6 | 10.3 | 90 | 13.9639 | 0.68748 | 14.5116 | [5 empty] | 0.91 | 14.0664 | 0.14066 |  | 0.28203
11:39 | 3972 | 68 | 262.5 | 10.3 | 91 | 14.0664 | 0.68761 | 14.5166 | [5 empty] | 0.92 | 14.2758 | 0.14171
11:39 | 3969 | 68 | 262.5 | 10.4 | 92 | 14.0664 | 0.68761 | 14.5211 | [5 empty] | 0.93 | 14.2784 | 0.14277 |  | 0.28556
11:39 | 3965 | 70 | 262.8 | 10.4 | 93 | 14.2758 | 0.68722 | 14.5249 | [5 empty] | 0.94 | 14.2784 | 0.14278
11:39 | 3967 | 70 | 263 | 10.4 | 94 | 14.2784 | 0.68697 | 14.5283 | [5 empty] | 0.95 | 14.3774 | 0.14328 |  | 0.28822
11:39 | 3977 | 70 | 263 | 10.4 | 95 | 14.2784 | 0.68697 | 14.5313 | [5 empty] | 0.96 | 14.6793 | 0.14528
11:39 | 3977 | 71 | 262.8 | 10.4 | 96 | 14.3774 | 0.68722 | 14.5338 | [5 empty] | 0.97 | 14.9753 | 0.14827 |  | 0.29852
11:39 | 3968 | 74 | 262.9 | 10.4 | 97 | 14.6793 | 0.6871 | 14.5361 | [5 empty] | 0.98 | 14.9753 | 0.14975
11:39 | 3968 | 77 | 263 | 10.4 | 98 | 14.9753 | 0.68697 | 14.538 | [5 empty] | 0.99 | 14.9725 | 0.14974 |  | 0.29946
11:39 | 3959 | 77 | 263 | 10.4 | 99 | 14.9753 | 0.68697 | 14.5397 | [5 empty] | 1 | 14.9725 | 0.14973
11:39 | 3952 | 77 | 262.8 | 10.4 | 100 | 14.9725 | 0.68722 | 14.5411 | [5 empty] | 0 | 14.4783 | -14.7254 |  | -14.4153
11:39 | 3949 | 77 | 262.8 | 10.4 | 101 | 14.9725 | 0.68722 | 14.5424 | [5 empty] | 0.01 | 14.4796 | 0.14479
11:39 | 3947 | 72 | 262.8 | 10.4 | 102 | 14.4783 | 0.68722 | 14.5435 | [5 empty] | 0.02 | 14.4796 | 0.1448 |  | 0.28958
11:39 | 3948 | 72 | 262.9 | 10.4 | 103 | 14.4796 | 0.6871 | 14.5445 | [5 empty] | 0.03 | 14.4769 | 0.14478
11:39 | 3954 | 72 | 262.9 | 10.4 | 104 | 14.4796 | 0.6871 | 14.5454 | [5 empty] | 0.04 | 14.4769 | 0.14477 |  | 0.28922
11:39 | 3955 | 72 | 262.7 | 10.4 | 105 | 14.4769 | 0.68735 | 14.5462 | [5 empty] | 0.05 | 14.3814 | 0.14429
11:39 | 3963 | 72 | 262.7 | 10.4 | 106 | 14.4769 | 0.68735 | 14.5469 | [5 empty] | 0.06 | 14.3814 | 0.14381 |  | 0.28729
11:39 | 3963 | 71 | 263.1 | 10.4 | 107 | 14.3814 | 0.68684 | 14.5476 | [5 empty] | 0.07 | 14.2811 | 0.14331
11:39 | 3980 | 71 | 263.1 | 10.4 | 108 | 14.3814 | 0.68684 | 14.5482 | [5 empty] | 0.08 | 14.3841 | 0.14333 |  | 0.28834
11:39 | 3991 | 70 | 263.2 | 10.4 | 109 | 14.2811 | 0.68671 | 14.5488 | [5 empty] | 0.09 | 14.6834 | 0.14534
11:39 | 3997 | 71 | 263.3 | 10.4 | 110 | 14.3841 | 0.68658 | 14.5492 | [5 empty] | 0.1 | 14.6821 | 0.14683 |  | 0.2943
11:39 | 4003 | 74 | 263.2 | 10.4 | 111 | 14.6834 | 0.68671 | 14.5497 | [5 empty] | 0.11 | 14.8792 | 0.14781
11:39 | 4003 | 74 | 263.1 | 10.4 | 112 | 14.6821 | 0.68684 | 14.55 | [5 empty] | 0.12 | 15.0779 | 0.14979 |  | 0.30122
11:39 | 4000 | 76 | 263.1 | 10.4 | 113 | 14.8792 | 0.68684 | 14.5503 | [5 empty] | 0.13 | 15.1742 | 0.15126
11:39 | 3999 | 78 | 263.4 | 10.4 | 114 | 15.0779 | 0.68646 | 14.5505 | [5 empty] | 0.14 | 15.3594 | 0.15267 |  | 0.30657
11:39 | 3977 | 79 | 263.4 | 10.5 | 115 | 15.1742 | 0.68646 | 14.5506 | [5 empty] | 0.15 | 15.3594 | 0.15359
11:39 | 3977 | 81 | 263 | 10.4 | 116 | 15.3594 | 0.68697 | 14.5505 | [5 empty] | 0.16 | 15.3622 | 0.15361 |  | 0.30724
11:39 | 3968 | 81 | 263 | 10.4 | 117 | 15.3594 | 0.68697 | 14.5502 | [5 empty] | 0.17 | 15.3637 | 0.15363
11:39 | 3961 | 81 | 263.2 | 10.4 | 118 | 15.3622 | 0.68671 | 14.5498 | [5 empty] | 0.18 | 14.7851 | 0.15074 |  | 0.29763
11:39 | 3968 | 81 | 263.3 | 10.4 | 119 | 15.3637 | 0.68658 | 14.5492 | [5 empty] | 0.19 | 14.7865 | 0.14786
11:39 | 3976 | 75 | 263.4 | 10.4 | 120 | 14.7851 | 0.68646 | 14.5482 | [5 empty] | 0.2 | 14.588 | 0.14687 |  | 0.29175
11:39 | 3976 | 75 | 263.5 | 10.4 | 121 | 14.7865 | 0.68633 | 14.547 | [5 empty] | 0.21 | 14.3867 | 0.14487
11:39 | 3982 | 73 | 263.5 | 10.4 | 122 | 14.588 | 0.68633 | 14.5455 | [5 empty] | 0.22 | 14.3867 | 0.14387 |  | 0.28739
11:39 | 3982 | 71 | 263.5 | 10.4 | 123 | 14.3867 | 0.68633 | 14.5436 | [5 empty] | 0.23 | 14.2824 | 0.14335
11:39 | 3987 | 71 | 263.5 | 10.4 | 124 | 14.3867 | 0.68633 | 14.5412 | [5 empty] | 0.24 | 14.2824 | 0.14282 |  | 0.28599
11:39 | 3987 | 70 | 263.3 | 10.4 | 125 | 14.2824 | 0.68658 | 14.5384 | [5 empty] | 0.25 | 14.3854 | 0.14334
11:39 | 3988 | 70 | 263.3 | 10.4 | 126 | 14.2824 | 0.68658 | 14.5351 | [5 empty] | 0.26 | 14.3854 | 0.14385 |  | 0.28771
11:39 | 3988 | 71 | 263.4 | 10.4 | 127 | 14.3854 | 0.68646 | 14.5312 | [5 empty] | 0.27 | 14.3867 | 0.14386
11:39 | 3990 | 71 | 263.4 | 10.4 | 128 | 14.3854 | 0.68646 | 14.5267 | [5 empty] | 0.28 | 14.3881 | 0.14387 |  | 0.28742
11:39 | 3991 | 71 | 263.5 | 10.4 | 129 | 14.3867 | 0.68633 | 14.5215 | [5 empty] | 0.29 | 14.2864 | 0.14337
11:39 | 3991 | 71 | 263.6 | 10.4 | 130 | 14.3881 | 0.6862 | 14.5156 | [5 empty] | 0.3 | 14.0821 | 0.14184 |  | 0.28335
11:39 | 3993 | 70 | 263.6 | 10.4 | 131 | 14.2864 | 0.6862 | 14.5089 | [5 empty] | 0.31 | 14.3894 | 0.14236
11:39 | 3993 | 68 | 263.7 | 10.4 | 132 | 14.0821 | 0.68607 | 14.5013 | [5 empty] | 0.32 | 14.7865 | 0.14588 |  | 0.29441
11:39 | 3996 | 71 | 263.7 | 10.3 | 133 | 14.3894 | 0.68607 | 14.4929 | [5 empty] | 0.33 | 14.7865 | 0.14786
11:39 | 3996 | 75 | 263.5 | 10.4 | 134 | 14.7865 | 0.68633 | 14.4835 | [5 empty] | 0.34 | 15.0779 | 0.14932 |  | 0.30059
11:39 | 3997 | 75 | 263.5 | 10.4 | 135 | 14.7865 | 0.68633 | 14.4731 | [5 empty] | 0.35 | 15.0779 | 0.15078
11:39 | 3998 | 78 | 263.4 | 10.4 | 136 | 15.0779 | 0.68646 | 14.4616 | [5 empty] | 0.36 | 15.0751 | 0.15076 |  | 0.3015
11:39 | 3999 | 78 | 263.4 | 10.4 | 137 | 15.0779 | 0.68646 | 14.449 | [5 empty] | 0.37 | 15.0723 | 0.15074
11:39 | 4000 | 78 | 263.2 | 10.4 | 138 | 15.0751 | 0.68671 | 14.4352 | [5 empty] | 0.38 | 14.9753 | 0.15024 |  | 0.29982
11:39 | 4000 | 78 | 263 | 10.4 | 139 | 15.0723 | 0.68697 | 14.4202 | [5 empty] | 0.39 | 14.9739 | 0.14975
11:39 | 3999 | 77 | 263 | 10.4 | 140 | 14.9753 | 0.68697 | 14.4039 | [5 empty] | 0.4 | 14.5798 | 0.14777 |  | 0.29156
11:39 | 3999 | 77 | 262.9 | 10.4 | 141 | 14.9739 | 0.6871 | 14.3862 | [5 empty] | 0.41 | 14.1761 | 0.14378
11:39 | 3992 | 73 | 262.9 | 10.3 | 142 | 14.5798 | 0.6871 | 14.3672 | [5 empty] | 0.42 | 14.1761 | 0.14176 |  | 0.28353
11:39 | 3992 | 69 | 263 | 10.3 | 143 | 14.1761 | 0.68697 | 14.3467 | [5 empty] | 0.43 | 14.1774 | 0.14177
11:39 | 3999 | 69 | 263 | 10.3 | 144 | 14.1761 | 0.68697 | 14.3247 | [5 empty] | 0.44 | 14.1787 | 0.14178 |  | 0.28492
11:39 | 4006 | 69 | 263.1 | 10.3 | 145 | 14.1774 | 0.68684 | 14.3012 | [5 empty] | 0.45 | 14.5852 | 0.14382
11:39 | 4000 | 69 | 263.2 | 10.3 | 146 | 14.1787 | 0.68671 | 14.2761 | [5 empty] | 0.46 | 14.6875 | 0.14636 |  | 0.29274
11:39 | 3993 | 73 | 263.3 | 10.3 | 147 | 14.5852 | 0.68658 | 14.2494 | [5 empty] | 0.47 | 14.4877 | 0.14588
11:39 | 3992 | 74 | 263.5 | 10.3 | 148 | 14.6875 | 0.68633 | 14.2211 | [5 empty] | 0.48 | 14.3881 | 0.14438 |  | 0.28707
11:39 | 3977 | 72 | 263.5 | 10.3 | 149 | 14.4877 | 0.68633 | 14.1911 | [5 empty] | 0.49 | 14.0808 | 0.14234
11:39 | 3977 | 71 | 263.6 | 10.3 | 150 | 14.3881 | 0.6862 | 14.1594 | [5 empty] | 0.5 | 13.8696 | 0.13975 |  | 0.27809
11:39 | 3969 | 68 | 263.6 | 10.3 | 151 | 14.0808 | 0.6862 | 14.1259 | [5 empty] | 0.51 | 13.8683 | 0.13869
11:39 | 3969 | 66 | 263.4 | 10.3 | 152 | 13.8696 | 0.68646 | 14.0908 | [5 empty] | 0.52 | 13.6579 | 0.13763 |  | 0.27386
11:39 | 3965 | 66 | 263.3 | 10.3 | 153 | 13.8683 | 0.68658 | 14.0539 | [5 empty] | 0.53 | 13.6579 | 0.13658
11:39 | 3961 | 64 | 263.4 | 10.3 | 154 | 13.6579 | 0.68646 | 14.0152 | [5 empty] | 0.54 | 13.3339 | 0.13496 |  | 0.26776
11:39 | 3962 | 64 | 263.4 | 10.3 | 155 | 13.6579 | 0.68646 | 13.9749 | [5 empty] | 0.55 | 13.3339 | 0.13334
11:39 | 3964 | 61 | 263.4 | 10.3 | 156 | 13.3339 | 0.68646 | 13.9328 | [5 empty] | 0.56 | 13.6579 | 0.13496 |  | 0.27279
11:39 | 3963 | 61 | 263.4 | 10.3 | 157 | 13.3339 | 0.68646 | 13.889 | [5 empty] | 0.57 | 13.8709 | 0.13764
11:39 | 3956 | 64 | 263.4 | 10.3 | 158 | 13.6579 | 0.68646 | 13.8435 | [5 empty] | 0.58 | 13.8709 | 0.13871 |  | 0.27707
11:39 | 3956 | 66 | 263.5 | 10.3 | 159 | 13.8709 | 0.68633 | 13.7963 | [5 empty] | 0.59 | 13.7654 | 0.13818
11:39 | 3951 | 66 | 263.5 | 10.3 | 160 | 13.8709 | 0.68633 | 13.7475 | [5 empty] | 0.6 | 13.7654 | 0.13765 |  | 0.27388
11:39 | 3951 | 65 | 263.5 | 10.3 | 161 | 13.7654 | 0.68633 | 13.6972 | [5 empty] | 0.61 | 13.3376 | 0.13552
11:39 | 3950 | 65 | 263.5 | 10.3 | 162 | 13.7654 | 0.68633 | 13.6454 | [5 empty] | 0.62 | 13.3401 | 0.13339 |  | 0.26752
11:39 | 3948 | 61 | 263.7 | 10.3 | 163 | 13.3376 | 0.68607 | 13.5922 | [5 empty] | 0.63 | 13.5571 | 0.13449
11:39 | 3948 | 61 | 263.9 | 10.3 | 164 | 13.3401 | 0.68582 | 13.5376 | [5 empty] | 0.64 | 13.5571 | 0.13557 |  | 0.27042
11:39 | 3948 | 63 | 263.9 | 10.3 | 165 | 13.5571 | 0.68582 | 13.4817 | [5 empty] | 0.65 | 13.3401 | 0.13449
11:39 | 3948 | 63 | 263.9 | 10.3 | 166 | 13.5571 | 0.68582 | 13.4247 | [5 empty] | 0.66 | 13.0067 | 0.13173 |  | 0.26125
11:39 | 3955 | 61 | 263.9 | 10.3 | 167 | 13.3401 | 0.68582 | 13.3667 | [5 empty] | 0.67 | 13.0067 | 0.13007
11:39 | 3955 | 58 | 263.8 | 10.3 | 168 | 13.0067 | 0.68594 | 13.3077 | [5 empty] | 0.68 | 13.0019 | 0.13004 |  | 0.26005
11:39 | 3969 | 58 | 263.8 | 10.3 | 169 | 13.0067 | 0.68594 | 13.248 | [5 empty] | 0.69 | 13.0007 | 0.13001
11:39 | 3970 | 58 | 263.4 | 10.3 | 170 | 13.0019 | 0.68646 | 13.1877 | [5 empty] | 0.7 | 12.5444 | 0.12773 |  | 0.25241
11:39 | 3975 | 58 | 263.3 | 10.3 | 171 | 13.0007 | 0.68658 | 13.1269 | [5 empty] | 0.71 | 12.5456 | 0.12545
11:39 | 3980 | 54 | 263.3 | 10.3 | 172 | 12.5444 | 0.68658 | 13.0658 | [5 empty] | 0.72 | 12.5456 | 0.12546 |  | 0.25091
11:39 | 3981 | 54 | 263.4 | 10.4 | 173 | 12.5456 | 0.68646 | 13.0047 | [5 empty] | 0.73 | 12.5456 | 0.12546
11:39 | 3981 | 54 | 263.4 | 10.4 | 174 | 12.5456 | 0.68646 | 12.9437 | [5 empty] | 0.74 | 12.4288 | 0.12487 |  | 0.24858
11:39 | 3980 | 54 | 263.4 | 10.3 | 175 | 12.5456 | 0.68646 | 12.8831 | [5 empty] | 0.75 | 12.3122 | 0.12371
11:39 | 3976 | 53 | 263.4 | 10.3 | 176 | 12.4288 | 0.68646 | 12.8231 | [5 empty] | 0.76 | 12.3122 | 0.12312 |  | 0.24625
11:39 | 3976 | 52 | 263.5 | 10.3 | 177 | 12.3122 | 0.68633 | 12.764 | [5 empty] | 0.77 | 12.3145 | 0.12313
11:39 | 3985 | 52 | 263.5 | 10.3 | 178 | 12.3122 | 0.68633 | 12.706 | [5 empty] | 0.78 | 12.3145 | 0.12314 |  | 0.24629
11:39 | 3986 | 52 | 263.7 | 10.3 | 179 | 12.3145 | 0.68607 | 12.6495 | [5 empty] | 0.79 | 12.3156 | 0.12315
11:39 | 3994 | 52 | 263.7 | 10.3 | 180 | 12.3145 | 0.68607 | 12.5948 | [5 empty] | 0.8 | 12.3168 | 0.12316 |  | 0.24513
11:39 | 4000 | 52 | 263.8 | 10.3 | 181 | 12.3156 | 0.68594 | 12.5421 | [5 empty] | 0.81 | 11.9562 | 0.12136
11:39 | 4004 | 52 | 263.9 | 10.3 | 182 | 12.3168 | 0.68582 | 12.492 | [5 empty] | 0.82 | 11.8336 | 0.11895 |  | 0.23749
11:39 | 4010 | 49 | 263.9 | 10.3 | 183 | 11.9562 | 0.68582 | 12.4447 | [5 empty] | 0.83 | 11.9562 | 0.11895
11:39 | 4011 | 48 | 263.9 | 10.3 | 184 | 11.8336 | 0.68582 | 12.4006 | [5 empty] | 0.84 | 12.0753 | 0.12016 |  | 0.24151
11:39 | 4019 | 49 | 263.9 | 10.3 | 185 | 11.9562 | 0.68582 | 12.3602 | [5 empty] | 0.85 | 12.1955 | 0.12135
11:39 | 4019 | 50 | 263.7 | 10.3 | 186 | 12.0753 | 0.68607 | 12.3239 | [5 empty] | 0.86 | 12.3168 | 0.12256 |  | 0.24593
11:39 | 4016 | 51 | 263.7 | 10.3 | 187 | 12.1955 | 0.68607 | 12.2922 | [5 empty] | 0.87 | 12.3179 | 0.12317
11:39 | 4016 | 52 | 263.9 | 10.3 | 188 | 12.3168 | 0.68582 | 12.2656 | [5 empty] | 0.88 | 12.5514 | 0.12435 |  | 0.25025
11:39 | 4010 | 52 | 264 | 10.4 | 189 | 12.3179 | 0.68569 | 12.2446 | [5 empty] | 0.89 | 12.5502 | 0.12551
11:39 | 4004 | 54 | 263.9 | 10.3 | 190 | 12.5514 | 0.68582 | 12.2297 | [5 empty] | 0.9 | 12.5502 | 0.1255 |  | 0.251
11:39 | 4002 | 54 | 263.8 | 10.3 | 191 | 12.5502 | 0.68594 | 12.2215 | [5 empty] | 0.91 | 12.5491 | 0.1255
11:39 | 3998 | 54 | 263.8 | 10.3 | 192 | 12.5502 | 0.68594 | 12.2206 | [5 empty] | 0.92 | 12.6647 | 0.12607 |  | 0.25292
11:39 | 3998 | 54 | 263.7 | 10.3 | 193 | 12.5491 | 0.68607 | 12.2276 | [5 empty] | 0.93 | 12.6671 | 0.12666
11:39 | 3996 | 55 | 263.7 | 10.3 | 194 | 12.6647 | 0.68607 | 12.2432 | [5 empty] | 0.94 | 12.8953 | 0.12781 |  | 0.25791
11:39 | 3996 | 55 | 263.9 | 10.3 | 195 | 12.6671 | 0.68582 | 12.2681 | [5 empty] | 0.95 | 13.1233 | 0.13009
11:39 | 3996 | 57 | 263.9 | 10.4 | 196 | 12.8953 | 0.68582 | 12.303 | [5 empty] | 0.96 | 13.1245 | 0.13124 |  | 0.26322
11:39 | 3996 | 59 | 264.2 | 10.4 | 197 | 13.1233 | 0.68543 | 12.3485 | [5 empty] | 0.97 | 13.3451 | 0.13235
11:39 | 3992 | 59 | 264.3 | 10.4 | 198 | 13.1245 | 0.68531 | 12.4055 | [5 empty] | 0.98 | 13.3439 | 0.13344 |  | 0.26688
11:39 | 3989 | 61 | 264.3 | 10.4 | 199 | 13.3451 | 0.68531 | 12.4749 | [5 empty] | 0.99 | 13.3439 | 0.13344
11:39 | 3988 | 61 | 264.2 | 10.4 | 200 | 13.3439 | 0.68543 | 12.5573 | [5 empty] | 1 | 13.3401 | 0.13342
11:39 | 3987 | 61 | 264.2 | 10.4 | 201 | 13.3439 | 0.68543 | 12.6537
11:39 | 3987 | 61 | 263.9 | 10.4 | 202 | 13.3401 | 0.68582 | 12.7651
11:39 | 3982 | 62 | 263.9 | 10.4 | 203 | 13.449 | 0.68582 | 12.8923
11:39 | 3982 | 62 | 263.7 | 10.4 | 204 | 13.4465 | 0.68607 | 13.0363
11:39 | 3987 | 61 | 263.7 | 10.3 | 205 | 13.3376 | 0.68607 | 13.1981
11:39 | 3988 | 60 | 263.9 | 10.3 | 206 | 13.2303 | 0.68582 | 13.3788
11:39 | 3981 | 60 | 263.9 | 10.4 | 207 | 13.2303 | 0.68582 | 13.5794
11:39 | 3974 | 59 | 263.9 | 10.4 | 208 | 13.1196 | 0.68582 | 13.8012
11:39 | 3973 | 59 | 263.9 | 10.4 | 209 | 13.1196 | 0.68582 | 14.0452
11:39 | 3972 | 56 | 263.8 | 10.4 | 210 | 12.7805 | 0.68594 | 14.3127
11:39 | 3971 | 55 | 263.6 | 10.4 |  | 12.6635 | 0.6862
11:39 | 3964 | 55 | 263.7 | 10.4 |  | 12.6647 | 0.68607
11:39 | 3964 | 54 | 263.9 | 10.4 |  | 12.5514 | 0.68582
11:39 | 3958 | 55 | 263.9 | 10.4 |  | 12.6671 | 0.68582
11:39 | 3956 | 57 | 263.8 | 10.4 |  | 12.8941 | 0.68594
11:39 | 3959 | 57 | 263.7 | 10.4 |  | 12.8929 | 0.68607
11:39 | 3963 | 51 | 263.6 | 10.4 |  | 12.1944 | 0.6862
11:39 | 3964 | 51 | 263.6 | 10.4 |  | 12.1944 | 0.6862
11:39 | 3966 | 54 | 263.7 | 10.4 |  | 12.5491 | 0.68607
11:39 | 3967 | 55 | 263.7 | 10.4 |  | 12.6647 | 0.68607
11:39 | 3971 | 57 | 263.7 | 10.4 |  | 12.8929 | 0.68607
11:39 | 3971 | 58 | 264 | 10.4 |  | 13.0092 | 0.68569
11:39 | 3965 | 59 | 264 | 10.4 |  | 13.1208 | 0.68569
11:39 | 3963 | 61 | 263.9 | 10.4 |  | 13.3401 | 0.68582
11:39 | 3955 | 61 | 263.8 | 10.4 |  | 13.3389 | 0.68594
11:39 | 3948 | 57 | 263.6 | 10.4 |  | 12.8917 | 0.6862
11:39 | 3954 | 57 | 263.5 | 10.3 |  | 12.8905 | 0.68633
11:39 | 3967 | 53 | 263.5 | 10.3 |  | 12.43 | 0.68633
11:39 | 3968 | 52 | 263.3 | 10.3 |  | 12.3099 | 0.68658
11:39 | 3986 | 52 | 263.3 | 10.3 |  | 12.3099 | 0.68658
11:39 | 3986 | 53 | 263.3 | 10.3 |  | 12.4277 | 0.68658
11:39 | 3987 | 53 | 263.3 | 10.3 |  | 12.4277 | 0.68658
11:39 | 3987 | 53 | 263.2 | 10.3 |  | 12.4265 | 0.68671
11:39 | 3985 | 53 | 263.1 | 10.3 |  | 12.4254 | 0.68684
11:39 | 3983 | 51 | 263.1 | 10.3 |  | 12.1887 | 0.68684
11:39 | 3983 | 51 | 263.1 | 10.2 |  | 12.1887 | 0.68684
11:39 | 3983 | 50 | 263.1 | 10.2 |  | 12.0686 | 0.68684
11:39 | 3983 | 50 | 263.2 | 10.2 |  | 12.0697 | 0.68671
11:39 | 3985 | 50 | 263.2 | 10.2 |  | 12.0697 | 0.68671
11:39 | 3985 | 50 | 263.4 | 10.2 |  | 12.072 | 0.68646
11:39 | 3996 | 50 | 263.4 | 10.2 |  | 12.072 | 0.68646
11:39 | 4001 | 50 | 263.5 | 10.2 |  | 12.0731 | 0.68633
11:39 | 4004 | 50 | 263.5 | 10.3 |  | 12.0731 | 0.68633
11:39 | 4007 | 50 | 263.4 | 10.3 |  | 12.072 | 0.68646
11:39 | 4006 | 50 | 263.3 | 10.3 |  | 12.0708 | 0.68658
11:39 | 4004 | 50 | 263.2 | 10.3 |  | 12.0697 | 0.68671
11:39 | 4004 | 50 | 263 | 10.3 |  | 12.0675 | 0.68697
11:39 | 3987 | 52 | 263 | 10.3 |  | 12.3064 | 0.68697
11:39 | 3987 | 53 | 262.6 | 10.3 |  | 12.4196 | 0.68748
11:39 | 3978 | 54 | 262.6 | 10.3 |  | 12.5362 | 0.68748
11:39 | 3974 | 55 | 262.6 | 10.3 |  | 12.6517 | 0.68748
11:39 | 3966 | 55 | 262.5 | 10.3 |  | 12.6506 | 0.68761
11:39 | 3958 | 55 | 262.6 | 10.3 |  | 12.6517 | 0.68748
11:39 | 3958 | 55 | 262.6 | 10.3 |  | 12.6517 | 0.68748
11:39 | 3958 | 55 | 262.7 | 10.3 |  | 12.6529 | 0.68735
11:39 | 3959 | 56 | 262.9 | 10.3 |  | 12.7698 | 0.6871
11:39 | 3962 | 56 | 262.9 | 10.3 |  | 12.7698 | 0.6871
11:39 | 3962 | 56 | 262.6 | 10.3 |  | 12.7662 | 0.68748
11:39 | 3964 | 56 | 262.6 | 10.3 |  | 12.7662 | 0.68748
11:39 | 3965 | 55 | 262.7 | 10.3 |  | 12.6529 | 0.68735
11:39 | 3968 | 55 | 262.8 | 10.3 |  | 12.6541 | 0.68722
11:39 | 3972 | 54 | 262.6 | 10.3 |  | 12.5362 | 0.68748
11:39 | 3970 | 54 | 262.5 | 10.3 |  | 12.535 | 0.68761
11:39 | 3961 | 56 | 262.5 | 10.3 |  | 12.765 | 0.68761
11:39 | 3961 | 57 | 262.2 | 10.3 |  | 12.8749 | 0.68799
11:39 | 3954 | 56 | 262.2 | 10.3 |  | 12.7615 | 0.68799
11:39 | 3954 | 56 | 262.4 | 10.3 |  | 12.7639 | 0.68774
11:39 | 3950 | 56 | 262.4 | 10.3 |  | 12.7639 | 0.68774
11:39 | 3948 | 56 | 262.4 | 10.3 |  | 12.7639 | 0.68774
11:39 | 3945 | 56 | 262.5 | 10.3 |  | 12.765 | 0.68761
11:39 | 3942 | 55 | 262.4 | 10.3 |  | 12.6494 | 0.68774
11:39 | 3941 | 55 | 262.4 | 10.3 |  | 12.6494 | 0.68774
11:39 | 3932 | 56 | 262.4 | 10.3 |  | 12.7639 | 0.68774
11:39 | 3932 | 57 | 262.6 | 10.3 |  | 12.8797 | 0.68748
11:39 | 3935 | 55 | 262.6 | 10.3 |  | 12.6517 | 0.68748
11:39 | 3935 | 53 | 262.6 | 10.3 |  | 12.4196 | 0.68748
11:39 | 3948 | 53 | 262.6 | 10.3 |  | 12.4196 | 0.68748
11:39 | 3956 | 48 | 262.5 | 10.3 |  | 11.8181 | 0.68761
11:39 | 3968 | 49 | 262.5 | 10.3 |  | 11.9406 | 0.68761
11:39 | 3979 | 58 | 262.4 | 10.3 |  | 12.9898 | 0.68774
11:39 | 3977 | 58 | 262.4 | 10.3 |  | 12.9898 | 0.68774
11:39 | 3970 | 59 | 262.4 | 10.3 |  | 13.1013 | 0.68774
11:39 | 3970 | 60 | 262.5 | 10.3 |  | 13.2131 | 0.68761
11:39 | 3969 | 56 | 262.5 | 10.3 |  | 12.765 | 0.68761
11:39 | 3969 | 53 | 262.8 | 10.3 |  | 12.4219 | 0.68722
11:39 | 3969 | 53 | 262.8 | 10.4 |  | 12.4219 | 0.68722
11:39 | 3968 | 55 | 262.9 | 10.4 |  | 12.6553 | 0.6871
11:39 | 3974 | 55 | 263.1 | 10.4 |  | 12.6576 | 0.68684
11:39 | 3979 | 59 | 263.3 | 10.4 |  | 13.1123 | 0.68658
11:39 | 3979 | 59 | 263.5 | 10.4 |  | 13.1147 | 0.68633
11:39 | 3983 | 57 | 263.5 | 10.4 |  | 12.8905 | 0.68633
11:39 | 3983 | 56 | 263.9 | 10.4 |  | 12.7817 | 0.68582
11:39 | 3979 | 57 | 263.9 | 10.4 |  | 12.8953 | 0.68582
11:39 | 3979 | 58 | 263.8 | 10.4 |  | 13.0067 | 0.68594
11:39 | 3975 | 58 | 263.8 | 10.4 |  | 13.0067 | 0.68594
11:39 | 3972 | 61 | 263.7 | 10.4 |  | 13.3376 | 0.68607
11:39 | 3969 | 61 | 263.6 | 10.4 |  | 13.3364 | 0.6862
11:39 | 3966 | 65 | 263.7 | 10.4 |  | 13.768 | 0.68607
11:39 | 3965 | 65 | 263.8 | 10.4 |  | 13.7693 | 0.68594
11:39 | 3959 | 62 | 263.8 | 10.4 |  | 13.4478 | 0.68594
11:39 | 3959 | 60 | 263.8 | 10.4 |  | 13.2291 | 0.68594
11:39 | 3964 | 60 | 263.8 | 10.4 |  | 13.2291 | 0.68594
11:39 | 3964 | 61 | 263.8 | 10.4 |  | 13.3389 | 0.68594
11:39 | 3956 | 61 | 263.8 | 10.4 |  | 13.3389 | 0.68594
11:39 | 3950 | 65 | 263.9 | 10.4 |  | 13.7706 | 0.68582
11:39 | 3947 | 65 | 264 | 10.3 |  | 13.7718 | 0.68569
11:39 | 3944 | 61 | 264.1 | 10.3 |  | 13.3426 | 0.68556
11:39 | 3944 | 61 | 264.2 | 10.3 |  | 13.3439 | 0.68543
11:39 | 3945 | 62 | 264.2 | 10.3 |  | 13.4528 | 0.68543
11:39 | 3945 | 64 | 264.3 | 10.3 |  | 13.6693 | 0.68531
11:39 | 3944 | 65 | 264.3 | 10.3 |  | 13.7757 | 0.68531
11:39 | 3944 | 66 | 264.2 | 10.3 |  | 13.88 | 0.68543
11:39 | 3941 | 66 | 264.2 | 10.3 |  | 13.88 | 0.68543
11:39 | 3940 | 64 | 264.3 | 10.3 |  | 13.6693 | 0.68531
11:39 | 3946 | 64 | 264.3 | 10.3 |  | 13.6693 | 0.68531
11:39 | 3953 | 59 | 264.5 | 10.3 |  | 13.1269 | 0.68505
11:39 | 3953 | 59 | 264.7 | 10.3 |  | 13.1294 | 0.6848
11:39 | 3955 | 61 | 264.7 | 10.3 |  | 13.3501 | 0.6848
11:39 | 3955 | 62 | 264.3 | 10.3 |  | 13.454 | 0.68531
11:39 | 3947 | 63 | 264.3 | 10.3 |  | 13.5621 | 0.68531
11:39 | 3947 | 64 | 264.3 | 10.3 |  | 13.6693 | 0.68531
11:39 | 3942 | 64 | 264.3 | 10.3 |  | 13.6693 | 0.68531
11:39 | 3939 | 67 | 264.3 | 10.3 |  | 13.986 | 0.68531
11:39 | 3938 | 67 | 264.3 | 10.3 |  | 13.986 | 0.68531
11:39 | 3937 | 62 | 264.1 | 10.3 |  | 13.4515 | 0.68556
11:39 | 3938 | 62 | 263.9 | 10.3 |  | 13.449 | 0.68582
11:39 | 3946 | 62 | 263.9 | 10.3 |  | 13.449 | 0.68582
11:39 | 3946 | 62 | 263.9 | 10.3 |  | 13.449 | 0.68582
11:39 | 3952 | 64 | 263.9 | 10.3 |  | 13.6642 | 0.68582
11:39 | 3952 | 67 | 264.1 | 10.3 |  | 13.9834 | 0.68556
11:39 | 3952 | 67 | 264.1 | 10.4 |  | 13.9834 | 0.68556
11:39 | 3952 | 62 | 264.3 | 10.4 |  | 13.454 | 0.68531
11:39 | 3958 | 62 | 264.5 | 10.4 |  | 13.4565 | 0.68505
11:39 | 3965 | 63 | 264.5 | 10.4 |  | 13.5646 | 0.68505
11:39 | 3965 | 63 | 264.5 | 10.4 |  | 13.5646 | 0.68505
11:39 | 3968 | 65 | 264.5 | 10.4 |  | 13.7783 | 0.68505
11:39 | 3968 | 67 | 264.6 | 10.4 |  | 13.9899 | 0.68492
11:39 | 3965 | 66 | 264.6 | 10.4 |  | 13.8851 | 0.68492
11:39 | 3964 | 64 | 264.4 | 10.4 |  | 13.6706 | 0.68518
11:39 | 3966 | 64 | 264.4 | 10.4 |  | 13.6706 | 0.68518
11:39 | 3968 | 64 | 264.4 | 10.4 |  | 13.6706 | 0.68518
11:39 | 3964 | 64 | 264.4 | 10.4 |  | 13.6706 | 0.68518
11:39 | 3958 | 68 | 264.4 | 10.4 |  | 14.0913 | 0.68518
11:39 | 3958 | 68 | 264.3 | 10.4 |  | 14.09 | 0.68531
11:39 | 3950 | 66 | 264.3 | 10.4 |  | 13.8813 | 0.68531
11:39 | 3950 | 64 | 264.7 | 10.4 |  | 13.6744 | 0.6848
11:39 | 3950 | 63 | 264.7 | 10.4 |  | 13.5671 | 0.6848
11:39 | 3950 | 61 | 264.6 | 10.4 |  | 13.3488 | 0.68492
11:39 | 3948 | 61 | 264.6 | 10.3 |  | 13.3488 | 0.68492
11:39 | 3946 | 58 | 264.5 | 10.3 |  | 13.0152 | 0.68505
11:39 | 3950 | 58 | 264.3 | 10.3 |  | 13.0128 | 0.68531
11:39 | 3956 | 56 | 264.3 | 10.3 |  | 12.7865 | 0.68531
11:39 | 3955 | 56 | 264.2 | 10.3 |  | 12.7853 | 0.68543
11:39 | 3950 | 56 | 264.2 | 10.3 |  | 12.7853 | 0.68543
11:39 | 3950 | 57 | 264.1 | 10.3 |  | 12.8977 | 0.68556
11:39 | 3938 | 59 | 264.1 | 10.3 |  | 13.1221 | 0.68556
11:39 | 3936 | 64 | 264.2 | 10.3 |  | 13.668 | 0.68543
11:39 | 3921 | 64 | 264.2 | 10.3 |  | 13.668 | 0.68543
11:39 | 3907 | 59 | 264.3 | 10.3 |  | 13.1245 | 0.68531
11:39 | 3903 | 59 | 264.3 | 10.2 |  | 13.1245 | 0.68531
11:39 | 3895 | 58 | 264.3 | 10.2 |  | 13.0128 | 0.68531
11:39 | 3895 | 57 | 264.2 | 10.2 |  | 12.8989 | 0.68543
11:39 | 3885 | 56 | 264.3 | 10.2 |  | 12.7865 | 0.68531
11:39 | 3885 | 55 | 264.3 | 10.2 |  | 12.6718 | 0.68531
11:39 | 3885 | 55 | 264.3 | 10.2 |  | 12.6718 | 0.68531
11:39 | 3885 | 55 | 264.5 | 10.2 |  | 12.6741 | 0.68505
11:39 | 3884 | 55 | 264.5 | 10.2 |  | 12.6741 | 0.68505
11:39 | 3882 | 56 | 264.2 | 10.2 |  | 12.7853 | 0.68543
11:39 | 3877 | 56 | 264 | 10.2 |  | 12.7829 | 0.68569
11:39 | 3868 | 61 | 264 | 10.2 |  | 13.3414 | 0.68569
11:39 | 3867 | 62 | 264 | 10.2 |  | 13.4503 | 0.68569
11:39 | 3849 | 65 | 264 | 10.2 |  | 13.7718 | 0.68569
11:39 | 3849 | 68 | 263.9 | 10.2 |  | 14.0848 | 0.68582
11:39 | 3841 | 69 | 263.9 | 10.2 |  | 14.1879 | 0.68582
11:39 | 3839 | 71 | 263.6 | 10.2 |  | 14.3881 | 0.6862
11:39 | 3843 | 71 | 263.5 | 10.2 |  | 14.3867 | 0.68633
11:39 | 3845 | 70 | 263.3 | 10.2 |  | 14.2824 | 0.68658
11:39 | 3842 | 70 | 263.1 | 10.2 |  | 14.2797 | 0.68684
11:39 | 3835 | 67 | 263.1 | 10.2 |  | 13.9704 | 0.68684
11:39 | 3835 | 67 | 263.1 | 10.2 |  | 13.9704 | 0.68684
11:39 | 3836 | 65 | 263.1 | 10.2 |  | 13.7603 | 0.68684
11:39 | 3836 | 64 | 263.2 | 10.2 |  | 13.6553 | 0.68671
11:39 | 3831 | 64 | 263.2 | 10.2 |  | 13.6553 | 0.68671
11:39 | 3829 | 64 | 263.2 | 10.2 |  | 13.6553 | 0.68671
11:39 | 3833 | 64 | 263.1 | 10.2 |  | 13.654 | 0.68684
11:39 | 3837 | 62 | 263.2 | 10.2 |  | 13.4403 | 0.68671
11:39 | 3843 | 62 | 263.3 | 10.2 |  | 13.4415 | 0.68658
11:39 | 3854 | 57 | 263.4 | 10.2 |  | 12.8893 | 0.68646
11:39 | 3855 | 56 | 263.5 | 10.2 |  | 12.777 | 0.68633
11:39 | 3873 | 55 | 263.5 | 10.2 |  | 12.6624 | 0.68633
11:40 | 3873 | 55 | 263.6 | 10.2 |  | 12.6635 | 0.6862
11:40 | 3884 | 55 | 263.6 | 10.2 |  | 12.6635 | 0.6862
11:40 | 3889 | 54 | 263.8 | 10.2 |  | 12.5502 | 0.68594
11:40 | 3894 | 54 | 263.9 | 10.2 |  | 12.5514 | 0.68582
11:40 | 3899 | 46 | 264.1 | 10.2 |  | 11.5866 | 0.68556
11:40 | 3904 | 46 | 264.1 | 10.2 |  | 11.5866 | 0.68556
11:40 | 3913 | 47 | 264.2 | 10.2 |  | 11.7129 | 0.68543
11:40 | 3914 | 47 | 264.4 | 10.2 |  | 11.7151 | 0.68518
11:40 | 3926 | 46 | 264.4 | 10.2 |  | 11.5898 | 0.68518
11:40 | 3926 | 45 | 264.1 | 10.2 |  | 11.4599 | 0.68556
11:40 | 3949 | 44 | 264.1 | 10.3 |  | 11.3319 | 0.68556
11:40 | 3957 | 42 | 264.2 | 10.3 |  | 11.0724 | 0.68543
11:40 | 3965 | 42 | 264.2 | 10.2 |  | 11.0724 | 0.68543
11:40 | 3973 | 41 | 264.1 | 10.3 |  | 10.9388 | 0.68556
11:40 | 3977 | 41 | 264 | 10.3 |  | 10.9377 | 0.68569
11:40 | 3989 | 45 | 264 | 10.3 |  | 11.4589 | 0.68569
11:40 | 3990 | 46 | 264.2 | 10.3 |  | 11.5876 | 0.68543
11:40 | 3996 | 45 | 264.2 | 10.3 |  | 11.461 | 0.68543
11:40 | 3996 | 43 | 264.1 | 10.3 |  | 11.2024 | 0.68556
11:40 | 4000 | 43 | 264.1 | 10.3 |  | 11.2024 | 0.68556
11:40 | 4002 | 42 | 263.9 | 10.3 |  | 11.0693 | 0.68582
11:40 | 4011 | 42 | 263.8 | 10.3 |  | 11.0683 | 0.68594
11:40 | 4019 | 39 | 263.9 | 10.3 |  | 10.6666 | 0.68582
11:40 | 4019 | 39 | 264 | 10.3 |  | 10.6676 | 0.68569
11:40 | 4019 | 40 | 264 | 10.3 |  | 10.8035 | 0.68569
11:40 | 4019 | 40 | 264.1 | 10.3 |  | 10.8045 | 0.68556
11:40 | 4010 | 37 | 264.1 | 10.3 |  | 10.3915 | 0.68556
11:40 | 4010 | 34 | 263.9 | 10.3 |  | 9.9594 | 0.68582
11:40 | 4007 | 34 | 263.9 | 10.3 |  | 9.9594 | 0.68582
11:40 | 4005 | 32 | 263.6 | 10.3 |  | 9.6594 | 0.6862
11:40 | 4000 | 32 | 263.4 | 10.3 |  | 9.6576 | 0.68646
11:40 | 3995 | 29 | 263.5 | 10.3 |  | 9.1946 | 0.68633
11:40 | 3996 | 29 | 263.6 | 10.3 |  | 9.1954 | 0.6862
11:40 | 3999 | 26 | 263.6 | 10.3 |  | 8.7068 | 0.6862
11:40 | 3999 | 24 | 263.8 | 10.3 |  | 8.3668 | 0.68594
11:40 | 3997 | 23 | 263.8 | 10.3 |  | 8.1907 | 0.68594
11:40 | 3997 | 23 | 264 | 10.3 |  | 8.1922 | 0.68569
11:40 | 3996 | 22 | 264 | 10.3 |  | 8.0121 | 0.68569
11:40 | 3995 | 19 | 263.9 | 10.3 |  | 7.4451 | 0.68582
11:40 | 3998 | 19 | 263.9 | 10.3 |  | 7.4451 | 0.68582
11:40 | 4002 | 14 | 263.9 | 10.3 |  | 6.3909 | 0.68582
11:40 | 4002 | 14 | 263.9 | 10.3 |  | 6.3909 | 0.68582
11:40 | 4001 | 14 | 263.8 | 10.3 |  | 6.3903 | 0.68594
11:40 | 4001 | 14 | 263.7 | 10.3 |  | 6.3897 | 0.68607
11:40 | 4003 | 12 | 263.6 | 10.3 |  | 5.9151 | 0.6862

## Sheet2
199 | 67
198 | 66
197 | 66
196 | 69
195 | 69
194 | 69
193 | 69
192 | 67
191 | 64
190 | 64
189 | 63
188 | 63
187 | 69
186 | 70
185 | 69
184 | 69
183 | 64
182 | 59
181 | 61
180 | 64
179 | 64
178 | 63
177 | 63
176 | 64
175 | 64
174 | 66
173 | 67
172 | 68
171 | 69
170 | 69
169 | 69
168 | 69
167 | 70
166 | 70
165 | 73
164 | 77
163 | 79
162 | 83
161 | 83
160 | 87
159 | 87
158 | 81
157 | 80
156 | 76
155 | 71
154 | 69
153 | 65
152 | 65
151 | 64
150 | 64
149 | 69
148 | 70
147 | 70
146 | 71
145 | 71
144 | 68
143 | 68
142 | 72
141 | 72
140 | 72
139 | 72
138 | 75
137 | 78
136 | 78
135 | 80
134 | 80
133 | 83
132 | 83
131 | 81
130 | 80
129 | 76
128 | 72
127 | 73
126 | 74
125 | 74
124 | 76
123 | 76
122 | 78
121 | 79
120 | 77
119 | 74
118 | 74
117 | 75
116 | 75
115 | 71
114 | 71
113 | 75
112 | 77
111 | 77
110 | 77
109 | 77
108 | 77
107 | 77
106 | 77
105 | 77
104 | 77
103 | 77
102 | 79
101 | 82
100 | 81
99 | 79
98 | 79
97 | 81
96 | 81
95 | 77
94 | 76
93 | 75
92 | 75
91 | 75
90 | 76
89 | 76
88 | 80
87 | 80
86 | 78
85 | 77
84 | 80
83 | 83
82 | 84
81 | 89
80 | 89
79 | 79
78 | 79
77 | 77
76 | 77
75 | 75
74 | 72
73 | 73
72 | 76
71 | 76
70 | 73
69 | 73
68 | 72
67 | 72
66 | 75
65 | 78
64 | 78
63 | 80
62 | 80
61 | 77
60 | 77
59 | 77
58 | 77
57 | 77
56 | 77
55 | 76
54 | 73
53 | 73
52 | 79
51 | 79
50 | 80
49 | 80
48 | 79
47 | 78
46 | 78
45 | 72
44 | 72
43 | 71
42 | 71
41 | 69
40 | 68
39 | 69
38 | 70
37 | 70
36 | 71
35 | 71
34 | 70
33 | 70
32 | 64
31 | 58
30 | 57
29 | 56
28 | 56
27 | 55
26 | 55
25 | 51
24 | 51
23 | 54
22 | 57
21 | 54
20 | 51
19 | 51
18 | 41
17 | 41
16 | 33
15 | 33
14 | 33
13 | 34
12 | 30
11 | 26
10 | 26
9 | 24
8 | 23
7 | 22
6 | 22
5 | 21
4 | 21
3 | 20
2 | 20
1 | 20

## Sheet3
1
Velocity Pressure
Pa
66.7506
Velocity Pressure
Pa
33 | 20 | 26.5 | 1
33 | 20 | 26.5 | 2
35 | 20 | 27.5 | 3
36 | 21 | 28.5 | 4
38 | 21 | 29.5 | 5
41 | 22 | 31.5 | 6
42 | 22 | 32 | 7
49 | 23 | 36 | 8
49 | 24 | 36.5 | 9
57 | 26 | 41.5 | 10
57 | 26 | 41.5 | 11
60 | 30 | 45 | 12
62 | 34 | 48 | 13
61 | 33 | 47 | 14
61 | 33 | 47 | 15
61 | 33 | 47 | 16
61 | 41 | 51 | 17
61 | 41 | 51 | 18
59 | 51 | 55 | 19
59 | 51 | 55 | 20
62 | 54 | 58 | 21
65 | 57 | 61 | 22
66 | 54 | 60 | 23
67 | 51 | 59 | 24
68 | 51 | 59.5 | 25
73 | 55 | 64 | 26
73 | 55 | 64 | 27
80 | 56 | 68 | 28
80 | 56 | 68 | 29
79 | 57 | 68 | 30
78 | 58 | 68 | 31
78 | 64 | 71 | 32
78 | 70 | 74 | 33
79 | 70 | 74.5 | 34
85 | 71 | 78 | 35
85 | 71 | 78 | 36
83 | 70 | 76.5 | 37
82 | 70 | 76 | 38
82 | 69 | 75.5 | 39
81 | 68 | 74.5 | 40
83 | 69 | 76 | 41
85 | 71 | 78 | 42
85 | 71 | 78 | 43
83 | 72 | 77.5 | 44
83 | 72 | 77.5 | 45
80 | 78 | 79 | 46
80 | 78 | 79 | 47
79 | 79 | 79 | 48
79 | 80 | 79.5 | 49
77 | 80 | 78.5 | 50
75 | 79 | 77 | 51
75 | 79 | 77 | 52
80 | 73 | 76.5 | 53
80 | 73 | 76.5 | 54
79 | 76 | 77.5 | 55
78 | 77 | 77.5 | 56
77 | 77 | 77 | 57
75 | 77 | 76 | 58
74 | 77 | 75.5 | 59
72 | 77 | 74.5 | 60
72 | 77 | 74.5 | 61
69 | 80 | 74.5 | 62
69 | 80 | 74.5 | 63
70 | 78 | 74 | 64
70 | 78 | 74 | 65
70 | 75 | 72.5 | 66
70 | 72 | 71 | 67
70 | 72 | 71 | 68
70 | 73 | 71.5 | 69
70 | 73 | 71.5 | 70
69 | 76 | 72.5 | 71
69 | 76 | 72.5 | 72
69 | 73 | 71 | 73
69 | 72 | 70.5 | 74
69 | 75 | 72 | 75
69 | 77 | 73 | 76
69 | 77 | 73 | 77
69 | 79 | 74 | 78
69 | 79 | 74 | 79
69 | 89 | 79 | 80
69 | 89 | 79 | 81
71 | 84 | 77.5 | 82
71 | 83 | 77 | 83
73 | 80 | 76.5 | 84
77 | 77 | 77 | 85
77 | 78 | 77.5 | 86
78 | 80 | 79 | 87
78 | 80 | 79 | 88
81 | 76 | 78.5 | 89
81 | 76 | 78.5 | 90
82 | 75 | 78.5 | 91
82 | 75 | 78.5 | 92
83 | 75 | 79 | 93
84 | 76 | 80 | 94
84 | 77 | 80.5 | 95
84 | 81 | 82.5 | 96
84 | 81 | 82.5 | 97
77 | 79 | 78 | 98
77 | 79 | 78 | 99
69 | 81 | 75 | 100
68 | 82 | 75 | 101
68 | 79 | 73.5 | 102
69 | 77 | 73 | 103
72 | 77 | 74.5 | 104
76 | 77 | 76.5 | 105
76 | 77 | 76.5 | 106
81 | 77 | 79 | 107
82 | 77 | 79.5 | 108
82 | 77 | 79.5 | 109
82 | 77 | 79.5 | 110
81 | 77 | 79 | 111
80 | 77 | 78.5 | 112
80 | 75 | 77.5 | 113
80 | 71 | 75.5 | 114
80 | 71 | 75.5 | 115
76 | 75 | 75.5 | 116
76 | 75 | 75.5 | 117
71 | 74 | 72.5 | 118
70 | 74 | 72 | 119
70 | 77 | 73.5 | 120
70 | 79 | 74.5 | 121
71 | 78 | 74.5 | 122
72 | 76 | 74 | 123
72 | 76 | 74 | 124
75 | 74 | 74.5 | 125
75 | 74 | 74.5 | 126
70 | 73 | 71.5 | 127
69 | 72 | 70.5 | 128
68 | 76 | 72 | 129
67 | 80 | 73.5 | 130
66 | 81 | 73.5 | 131
65 | 83 | 74 | 132
65 | 83 | 74 | 133
62 | 80 | 71 | 134
62 | 80 | 71 | 135
62 | 78 | 70 | 136
62 | 78 | 70 | 137
65 | 75 | 70 | 138
67 | 72 | 69.5 | 139
69 | 72 | 70.5 | 140
73 | 72 | 72.5 | 141
73 | 72 | 72.5 | 142
75 | 68 | 71.5 | 143
75 | 68 | 71.5 | 144
78 | 71 | 74.5 | 145
79 | 71 | 75 | 146
78 | 70 | 74 | 147
78 | 70 | 74 | 148
77 | 69 | 73 | 149
75 | 64 | 69.5 | 150
75 | 64 | 69.5 | 151
81 | 65 | 73 | 152
82 | 65 | 73.5 | 153
81 | 69 | 75 | 154
80 | 71 | 75.5 | 155
75 | 76 | 75.5 | 156
68 | 80 | 74 | 157
66 | 81 | 73.5 | 158
61 | 87 | 74 | 159
61 | 87 | 74 | 160
55 | 83 | 69 | 161
55 | 83 | 69 | 162
56 | 79 | 67.5 | 163
57 | 77 | 67 | 164
58 | 73 | 65.5 | 165
58 | 70 | 64 | 166
58 | 70 | 64 | 167
58 | 69 | 63.5 | 168
58 | 69 | 63.5 | 169
62 | 69 | 65.5 | 170
62 | 69 | 65.5 | 171
61 | 68 | 64.5 | 172
61 | 67 | 64 | 173
59 | 66 | 62.5 | 174
57 | 64 | 60.5 | 175
57 | 64 | 60.5 | 176
57 | 63 | 60 | 177
57 | 63 | 60 | 178
60 | 64 | 62 | 179
60 | 64 | 62 | 180
58 | 61 | 59.5 | 181
56 | 59 | 57.5 | 182
57 | 64 | 60.5 | 183
57 | 69 | 63 | 184
56 | 69 | 62.5 | 185
50 | 70 | 60 | 186
50 | 69 | 59.5 | 187
50 | 63 | 56.5 | 188
50 | 63 | 56.5 | 189
48 | 64 | 56 | 190
47 | 64 | 55.5 | 191
47 | 67 | 57 | 192
48 | 69 | 58.5 | 193
47 | 69 | 58 | 194
41 | 69 | 55 | 195
41 | 69 | 55 | 196
33 | 66 | 49.5 | 197
32 | 66 | 49 | 198
33 | 67 | 50 | 199
33 | 68 | 50.5 | 200
32 | 66 | 49 | 201
30 | 64 | 47 | 202
30 | 64 | 47 | 203
27 | 64 | 45.5 | 204
27 | 64 | 45.5 | 205
35 | 66 | 50.5 | 206
35 | 66 | 50.5 | 207
38 | 65 | 51.5 | 208
41 | 65 | 53 | 209
41 | 63 | 52 | 210
41 | 61 | 51 | 211
41 | 61 | 51 | 212
44 | 57 | 50.5 | 213
44 | 57 | 50.5 | 214
47 | 61 | 54 | 215
47 | 61 | 54 | 216
50 | 57 | 53.5 | 217
53 | 53 | 53 | 218
57 | 50 | 53.5 | 219
61 | 47 | 54 | 220
61 | 47 | 54 | 221
57 | 44 | 50.5 | 222
57 | 44 | 50.5 | 223
61 | 41 | 51 | 224
61 | 41 | 51 | 225
63 | 41 | 52 | 226
65 | 41 | 53 | 227
65 | 38 | 51.5 | 228
66 | 35 | 50.5 | 229
66 | 35 | 50.5 | 230
64 | 27 | 45.5 | 231
64 | 27 | 45.5 | 232
64 | 30 | 47 | 233
64 | 30 | 47 | 234
66 | 32 | 49 | 235
68 | 33 | 50.5 | 236
67 | 33 | 50 | 237
66 | 32 | 49 | 238
66 | 33 | 49.5 | 239
69 | 41 | 55 | 240
69 | 41 | 55 | 241
69 | 47 | 58 | 242
69 | 48 | 58.5 | 243
67 | 47 | 57 | 244
64 | 47 | 55.5 | 245
64 | 48 | 56 | 246
63 | 50 | 56.5 | 247
63 | 50 | 56.5 | 248
69 | 50 | 59.5 | 249
70 | 50 | 60 | 250
69 | 56 | 62.5 | 251
69 | 57 | 63 | 252
64 | 57 | 60.5 | 253
59 | 56 | 57.5 | 254
61 | 58 | 59.5 | 255
64 | 60 | 62 | 256
64 | 60 | 62 | 257
63 | 57 | 60 | 258
63 | 57 | 60 | 259
64 | 57 | 60.5 | 260
64 | 57 | 60.5 | 261
66 | 59 | 62.5 | 262
67 | 61 | 64 | 263
68 | 61 | 64.5 | 264
69 | 62 | 65.5 | 265
69 | 62 | 65.5 | 266
69 | 58 | 63.5 | 267
69 | 58 | 63.5 | 268
70 | 58 | 64 | 269
70 | 58 | 64 | 270
73 | 58 | 65.5 | 271
77 | 57 | 67 | 272
79 | 56 | 67.5 | 273
83 | 55 | 69 | 274
83 | 55 | 69 | 275
87 | 61 | 74 | 276
87 | 61 | 74 | 277
81 | 66 | 73.5 | 278
80 | 68 | 74 | 279
76 | 75 | 75.5 | 280
71 | 80 | 75.5 | 281
69 | 81 | 75 | 282
65 | 82 | 73.5 | 283
65 | 81 | 73 | 284
64 | 75 | 69.5 | 285
64 | 75 | 69.5 | 286
69 | 77 | 73 | 287
70 | 78 | 74 | 288
70 | 78 | 74 | 289
71 | 79 | 75 | 290
71 | 78 | 74.5 | 291
68 | 75 | 71.5 | 292
68 | 75 | 71.5 | 293
72 | 73 | 72.5 | 294
72 | 73 | 72.5 | 295
72 | 69 | 70.5 | 296
72 | 67 | 69.5 | 297
75 | 65 | 70 | 298
78 | 62 | 70 | 299
78 | 62 | 70 | 300
80 | 62 | 71 | 301
80 | 62 | 71 | 302
83 | 65 | 74 | 303
83 | 65 | 74 | 304
81 | 66 | 73.5 | 305
80 | 67 | 73.5 | 306
76 | 68 | 72 | 307
72 | 69 | 70.5 | 308
73 | 70 | 71.5 | 309
74 | 75 | 74.5 | 310
74 | 75 | 74.5 | 311
76 | 72 | 74 | 312
76 | 72 | 74 | 313
78 | 71 | 74.5 | 314
79 | 70 | 74.5 | 315
77 | 70 | 73.5 | 316
74 | 70 | 72 | 317
74 | 71 | 72.5 | 318
75 | 76 | 75.5 | 319
75 | 76 | 75.5 | 320
71 | 80 | 75.5 | 321
71 | 80 | 75.5 | 322
75 | 80 | 77.5 | 323
77 | 80 | 78.5 | 324
77 | 81 | 79 | 325
77 | 82 | 79.5 | 326
77 | 82 | 79.5 | 327
77 | 82 | 79.5 | 328
77 | 81 | 79 | 329
77 | 76 | 76.5 | 330
77 | 76 | 76.5 | 331
77 | 72 | 74.5 | 332
77 | 69 | 73 | 333
79 | 68 | 73.5 | 334
82 | 68 | 75 | 335
81 | 69 | 75 | 336
79 | 77 | 78 | 337
79 | 77 | 78 | 338
81 | 84 | 82.5 | 339
81 | 84 | 82.5 | 340
77 | 84 | 80.5 | 341
76 | 84 | 80 | 342
75 | 83 | 79 | 343
75 | 82 | 78.5 | 344
75 | 82 | 78.5 | 345
76 | 81 | 78.5 | 346
76 | 81 | 78.5 | 347
80 | 78 | 79 | 348
80 | 78 | 79 | 349
78 | 77 | 77.5 | 350
77 | 77 | 77 | 351
80 | 73 | 76.5 | 352
83 | 71 | 77 | 353
84 | 71 | 77.5 | 354
89 | 69 | 79 | 355
89 | 69 | 79 | 356
79 | 69 | 74 | 357
79 | 69 | 74 | 358
77 | 69 | 73 | 359
77 | 69 | 73 | 360
75 | 69 | 72 | 361
72 | 69 | 70.5 | 362
73 | 69 | 71 | 363
76 | 69 | 72.5 | 364
76 | 69 | 72.5 | 365
73 | 70 | 71.5
73 | 70 | 71.5
72 | 70 | 71
72 | 70 | 71
75 | 70 | 72.5
78 | 70 | 74
78 | 70 | 74
80 | 69 | 74.5
80 | 69 | 74.5
77 | 72 | 74.5
77 | 72 | 74.5
77 | 74 | 75.5
77 | 75 | 76
77 | 77 | 77
77 | 78 | 77.5
76 | 79 | 77.5
73 | 80 | 76.5
73 | 80 | 76.5
79 | 75 | 77
79 | 75 | 77
80 | 77 | 78.5
80 | 79 | 79.5
79 | 79 | 79
78 | 80 | 79
78 | 80 | 79
72 | 83 | 77.5
72 | 83 | 77.5
71 | 85 | 78
71 | 85 | 78
69 | 83 | 76
68 | 81 | 74.5
69 | 82 | 75.5
70 | 82 | 76
70 | 83 | 76.5
71 | 85 | 78
71 | 85 | 78
70 | 79 | 74.5
70 | 78 | 74
64 | 78 | 71
58 | 78 | 68
57 | 79 | 68
56 | 80 | 68
56 | 80 | 68
55 | 73 | 64
55 | 73 | 64
51 | 68 | 59.5
51 | 67 | 59
54 | 66 | 60
57 | 65 | 61
54 | 62 | 58
51 | 59 | 55
51 | 59 | 55
41 | 61 | 51
41 | 61 | 51
33 | 61 | 47
33 | 61 | 47
33 | 61 | 47
34 | 62 | 48
30 | 60 | 45
26 | 57 | 41.5
26 | 57 | 41.5
24 | 49 | 36.5
23 | 49 | 36
22 | 42 | 32
22 | 41 | 31.5
21 | 38 | 29.5
21 | 36 | 28.5
20 | 35 | 27.5
20 | 33 | 26.5
20 | 33 | 26.5